## Coverpage
Shungnak Energy Configuration Options
Energy Infrastructure Optimization to Reduce Fuel Cost and Dependence in Shungnak Alaska: Detailed Analysis
Publish Date:
DM Rosewater
JP Eddy
SAND2017-11620 O

## README
ASSUMPTIONS (Selected).
| Item | Base Case | Sensitivities | Comment
| Nominal Discount Rate | 3.5% | 7%
| Load Inflation Rate | 0.75% |  | Load calculated in 2028 and used as an average for the whole period
| Heating fuel cost ($/gal) | 7.99 | "-30%, -15%, +50%, +100%"
| Diesel oil cost ($/gal) | 7.1633 | "-30%, -15%, +50%, +100%"
Load
| Electrical Load Min | 0.63 kW
| Electrical Load Average | 199.45 kW |  | Load was average 180.99 kW in 2015. Assume Load inflation rate of 0.75% per year, Load calculated in 2028 and used as an average for the whole period
| Electrical Load Max | 399.46 kW
o Time series (10 min) data from 2015. (~70% data recovery).
| Heat Load Min | 1.6 kW |  | o Small gaps (up to 3 hours) filled by averaging from loads just prior and just after the gap
| Heat Load Average | 291.41 kW |  | o Large gaps filled by 1) Using data from 2016; 2) Copying data from prior to or after the gap.
| Heat Load Max | 1,551.37 kW |  | o File run through Windographer to convert to 60 min time steps
| Assume that waste heat is free to heating customers |  |  | Waste heat is not free, however it is much less expencive than heating fuel. As this analysis uses all waste heat avalible, regardless of price, we can role the opertunity cost of waste heat into the marginal cost of heating fuel.
Wind | Frontier F24 100 kW turbine |  |  | Frontier F24
| Cost | 900000 |  | o Power curve provided by Dennis Meiners.
| Operational Cost ($/year) | 17500 |  | o Hub height provided by Dennis Meiners.
| Capacity | 100 kWh |  | o Capital cost of $700,000 from discussions with Dennis Meiners. Assumed replacement cost of 80% of new cost. Per Dennis, reduced costs of each succeeding turbine, (up to 4 additional) by 5% each. Per ACEP report used a value of O&M of $17,500 per year. Reduced costs of each succeeding turbine, (up to 4 additional) by 5% each.
o Added fixed cost of $200,000 to the turbine cost to account for integration costs. So... the first turbine is $900,000, the second turbine is an additional $665,000, etc. Wind Resource
| WG 200 (2 turbines) |  |  | o Used measured data (10 min) from June 2012 - June 2013. Loaded into Windographer, QC'd, and filled gaps. o Exported hourly data file and reordered to create file running from Jan 1 - Dec 31. Integration o Assume $300,000 integration costs. Treat as a fixed cost applied as follows – Wind turbine: $200,000 -- Converter: $50,000 -- Batteries (Li-Ion): $50,000
| Cost | 1565000 |  | o Replacement cost of $560,000 for the first turbine with reduced costs of each succeeding turbine, (up to 4 additional) by 5% each.
| Operational Cost ($/year) | 34125
| Capacity | 200 kWh
WG 300
| Cost | 2196750
| Operational Cost ($/year) | 49875
| Capacity | 300 kWh
WG 400
| Cost | 2796912.5
| Operational Cost ($/year) | 64750
| Capacity | 400 kWh
WG 500
| Cost | 3367066.875
| Operational Cost ($/year) | 78750
| Capacity | 500 kWh
Solar | SG 100 |  |  | Using $5/W to be consistent with NREL. Installation Cost ~$3.5/Watt from AKAES Solar 042216 document.
| Cost | 500000
| Operational Cost (Dollars/Hour) | 0.54
| Capacity | 100 kWh
SG 200
| Cost | 1000000
| Operational Cost (Dollars/Hour) | 1.08
| Capacity | 200 kWh
SG 300
| Cost | 1500000
| Operational Cost (Dollars/Hour) | 1.62
| Capacity | 300 kWh
SG 500
| Cost | 2500000
| Operational Cost (Dollars/Hour) | 2.7
| Capacity | 500 kWh
Hydro | Shungnak Hydro
| Cost | 10318615
| Operational Cost | $0 Dollars/Hour
| Capacity | 235 kWh
Battery | Bat 100/100
| Cost | 257500 |  | Converter
| Operational Cost (per year) | 3000 |  | o Fixed cost: $50,000
| Charging Efficiencies | 89.44% |  | o Marginal cost (Up to 160 kW) $875/kW
| Discharging Efficiencies | 89.44% |  | o Marginal cost: (> 160 kW): $600/kW
| Energy Capacity | 100 kWh |  | o Replacement cost: 75% of initial cost
| Max Charge Rate | 100 kW |  | o O&M: $10/kW
| Max Discharge Rate | 100 kW
| Min State of Charge | 10% |  | Batteries
| Max State of Charge | 90% |  | o Fixed cost: $50,000
| Desired State of Charge | 0.7 |  | o Marginal cost (Up to 200 kWh) $700/kWh
o Marginal cost: (> 200 kWh): $480/kWh
| Bat 50/50 |  |  | o Replacement cost: 75% of initial cost
| Cost | 178750 |  | o O&M: $20/kWh
| Operational Cost | 1500
| Charging Efficiencies | 89.44%
| Discharging Efficiencies | 89.44%
| Energy Capacity | 100 kWh
| Max Charge Rate | 100 kW
| Max Discharge Rate | 100 kW
| Min State of Charge | 10%
| Max State of Charge | 90%
| Desired State of Charge | 0.7
Stove Heating System
| Simulation takes spilled wind/solar and uses converts it to heat energy |  | Thermal Load Controller Per conversations with Dennis
| Efficiency | 98% | o Fixed cost: $10,000 o Marginal cost: $3,000 per (6 kW) stove)
| Integration Cost | 10000
| Cost per stove | 3000
| Stove Power per unit (kW) | 6

## NO-EE Detailed
Simulation Statistics "CASE NUMBER" | 45
Total Sim Time | 219000
Power Utility Statistics
Failure Statistics
Occurrences | 1 (all attributed to "Islanded Operations")
Downtime
Min | 219,000 hrs
Max | 219,000 hrs
Average | 219,000 hrs
Total | 219,000 hrs
Thermal Load Service
Overall
Overall Energy Availability | 20.56%
DBT Occurrences w/ Load Loss | 100%
Total Load Served | 14457633.54 | 70329066.63
Total Load Not Served | 55871433.09
Post-Startup
Post-Startup Energy Availability | 20.56%
DBT Occurrences w/ Post-Startup Load Loss | 100%
Total Post-Startup Load Served | 14457633.54
Total Post-Startup Load Not Served | 55871433.09
Variable Selections
New Solar | No Generator
Hydro Stand-In | No Generator
New Wind | No Generator
New Storage | No Battery
Metric Values
Purchase Cost | 0
Energy Availability | 100%
Diesel Fuel Used | 14.77
Heating Fuel Deferred | 14943.28
Average Renewable Energy Spilled | 0
Diesel Utilization | 0.5847
Cost
Fixed Cost | 0
Variable Cost | 0
Total Cost | 0
Generation
Total Diesel Generation | 1278
Total Solar Generation
Total Wind Generation
Overall Diesel Efficiency | 34.88%
Overall Diesel Utilization | 58.47%
Solar Generated
Min | 0 kWh
Max | 0 kWh
Average | 0 kWh
Total | 0 kWh
Solar Spilled
Min | 0 kWh
Max | 0 kWh
Average | 0 kWh
Total | 0 kWh
Wind Generated
Min | 0 kWh
Max | 0 kWh
Average | 0 kWh
Total | 0 kWh
Wind Spilled
Min | 0 kWh
Max | 0 kWh
Average | 0 kWh
Total | 0 kWh
Weight
Fixed Weight | 0 lbs
Variable Weight | 0 lbs
Total Weight | 0 lbs
Volume
Fixed Volume | 0 cu ft
Variable Volume | 0 cu ft
Total Volume | 0 cu ft
Load
Aggregated
Min | 0.63 kW
Average | 199.45 kW
Max | 399.46 kW
Tier (Only) | Priority
Load Service
Priority
Overall
Overall Energy Availability | 100%
DBT Occurrences w/ Load Loss | 100%
Total Load Served | 43679901880
Total Load Not Served | 30.1 kWh
Post-Startup
Post-Startup Energy Availability | 100%
DBT Occurrences w/ Post-Startup Load Loss | 100%
Total Post-Startup Load Served | 43679901880
Total Post-Startup Load Not Served | 29.37 kWh
Startup Time
Min | 0.17 min
Max | 0.17 min
Average | 0.17 min
Renewable Penetration
Min | 0%
Max | 0%
Average | 0%
Histogram (% of DBT Time)
<= -100.00% | 0%
<= 0.00% | 0%
<= 25.00% | 0%
<= 50.00% | 0%
<= 75.00% | 0%
<= 100.00% | 0%
<= 110.00% | 0%
<= 120.00% | 0%
<= 130.00% | 0%
<= 140.00% | 0%
<= Infinity | 0%
Diesel Fuel Use
Min | 3235619.68 | 129424.7872
Max | 3,235,619.68 gal per outage
Average | 3,235,619.68 gal per outage
Natural Gas Use
Min | 0 MBTU per outage
Max | 0 MBTU per outage
Average | 0 MBTU per outage
Spinning Reserve
Min | 3.26%
Max | 100%
Average | 40.12%
Histogram (% of DBT Time)
<= -100.00% | 0%
<= 0.00% | 0%
<= 5.00% | 0%
<= 10.00% | 0.04%
<= 15.00% | 0.36%
<= 20.00% | 3.05%
<= 25.00% | 6.82%
<= 30.00% | 10.35%
<= 40.00% | 27.12%
<= 50.00% | 32.1%
<= 75.00% | 19.86%
<= 100.00% | 0.31%
<= Infinity | 0%
Diesel Gen Set Data
JD 6619 Run Time (hours/year) | 2369.872
CAT 3406 Run Time (hours/year) | 3295.62
SD 60 Run Time (hours/year) | 3843.3116
CMS K19G2 Run Time (hours/year) | 372.6012
Total Run Time | 9881.4048
JD 6619 Run Time (hours) | 59246.8 | 58557.69
CAT 3406 Run Time (hours) | 82390.5 | 79676.85
SD 60 Run Time (hours) | 96082.79 | 100164.17
CMS K19G2 Run Time (hours) | 9315.03 | 7994.95
Total Run Time | 247035.12 | 246393.66
Assumptions
Horizon (years) | 25
Nominal Discount Rate | 3%
Load Inflation Rate | 1%
Fuel Cost Adjustment | 1
Heating fuel cost ($/gal) | 7.99
Diesel oil cost ($/gal) | 7.1633
HHV (Btu/gallon) | 134000
Conversion (kWh/Btu) | 0.00029307
Baseline total fuel use (gal/year) | 186075.5898
Energy Efficiency Cost Electrical Curve | 0.1493
Energy Efficiency Cost Electrical Curve | -0.9009
Energy Efficiency Cost Electrical Curve | 16.515
Energy Efficiency Cost Thermal Curve | 0.1123
Energy Efficiency Cost Thermal Curve | -0.6774
Energy Efficiency Cost Thermal Curve | 12.418
Baseline electrical load (kWh/year) | 1747196.0752
Baseline thermal load (kWh/year) | 2813162.6652
EE electrical load(kWh/year) | 17471960.752
EE thermal load(kWh/year) | 2813162.6652
Assumed replacement usage (hours) | 80000
Gen replacement curve ($/kW) | 410.53
Gen replacement curve ($) | 105.26
202kW Gen O&M | 15.7808
314kW Gen O&M | 16.4528
365kW Gen O&M | 16.7588
397kW Gen O&M | 17.1422
EE electrical load reduction (%) | -9
EE thermal load reduction (%) | 0
EE electrical load reduction cost ($/kWh/year) | 1345.9724
EE thermal load reduction cost ($/kWh/year) | 0.1123
EE electrical load reduction cost ($/kWh/year) | 21165099251.4677
EE thermal load reduction cost ($/kWh/year) | 0
Financial calculations
Purchase Cost | 0
Stove Cost | 0
kW of Stoves | 0
# of Stoves | 0
Gen Replacement Cost (per year)
JD 6619 | -2459.6996
CAT 3406 | -5314.6684
SD 60 | -7203.7452
CMS | -759.574
Gen O&M Cost (per year)
JD 6619 | -37398.3576
CAT 3406 | -54222.012
SD 60 | -64409.0983
CMS | -6387.2209
Diesel Fuel use (Gal/year) | 129385.2
Heating Fuel use (Gal/year) | 56690.3898
Total Fuel usage (Gal/year) | 186075.5898
Gen O&M + Replacement Cost
Year
1 | -178154.3759
2 | -167927.5859
3 | -163036.4912
4 | -158287.8555
5 | -153677.5296
6 | -149201.4851
7 | -144855.8107
8 | -140636.7095
9 | -136540.4946
10 | -132563.587
11 | -128702.5117
12 | -124953.8948
13 | -121314.461
14 | -117781.0301
15 | -114350.5146
16 | -111019.9171
17 | -107786.3273
18 | -104646.9197
19 | -101598.9512
20 | -98639.7584
Total Gen O&M + Replacement Cost | -2655676.211
Diesel Fuel Cost
Year
1 | -926829.316
2 | -873625.5217
3 | -848180.1182
4 | -823475.8429
5 | -799491.1096
6 | -776204.9608
7 | -753597.0493
8 | -731647.6207
9 | -710337.4958
10 | -689648.0542
11 | -669561.2177
12 | -650059.4346
13 | -631125.6647
14 | -612743.3638
15 | -594896.4697
16 | -577569.388
17 | -560746.9787
18 | -544414.5424
19 | -528557.8082
20 | -513162.9205
Total Diesel Fuel Cost | -13815874.8773
Heating Fuel Cost
Year
1 | -452956.2143
2 | -426954.6746
3 | -414519.1015
4 | -402445.7296
5 | -390724.0094
6 | -379343.6984
7 | -368294.8528
8 | -357567.8183
9 | -347153.2216
10 | -337041.9627
11 | -327225.2065
12 | -317694.3753
13 | -308441.1411
14 | -299457.4185
15 | -290735.3578
16 | -282267.3376
17 | -274045.9589
18 | -266064.0377
19 | -258314.5997
20 | -250790.8735
Total Heating Fuel Cost | -6752037.5899
Total Net Present Cost | 21141875662.7895
Note on B1: Author: As Energy Efficiency is the first, least expensive option, the only case used from this sheet is the Baseline case
Note on A197: Author: Already Included in Purchase Cost

## Genset O&M Costs
Diesel Plant O&M (ACEP Cost Model) (Diesel genset only, not plant)
Diesel Size (kW) | Load Factor (%) | O&M ($/kWh) | O&M ($/hr) | O&M ($/Hr/kWh)
50 | 0.55 | 0.53 | 14.575 | 0.2915
100 | 0.55 | 0.3 | 16.5 | 0.165
150 | 0.55 | 0.25 | 20.625 | 0.1375
202 |  |  | 21.041 | 0.10416
314 |  |  | 21.937 | 0.069863
365 |  |  | 22.345 | 0.061219
370 | 0.55 | 0.11 | 22.385 | 0.0605
397 |  |  | 22.8563 | 0.057573
600 | 0.55 | 0.08 | 26.4 | 0.044
950 | 0.55 | 0.052 | 27.17 | 0.0286
1300 | 0.55 | 0.04 | 28.6 | 0.022
Hourly O&M Costs adjusted to match AVEC non-fuel generating costs (2016) of $0.0955/kWh
(Multiply costs by 0.75)
0.75 | Adjustment factor
Diesel Size (kW) | Load Factor (%) | O&M ($/kWh) | O&M ($/hr) | O&M ($/Hr/kWh)
202 |  |  | 15.7808 | 0.078123
314 |  |  | 16.4528 | 0.052397
365 |  |  | 16.7588 | 0.045914
397 |  |  | 17.1422 | 0.043179
Source: ACEP , "Diesel Generator Technology Report"
o CAPEX values are for a diesel plant, not just the diesel generator
o OPEX values (modeled) assume 55% load factor. These are for the generator only. The RCA data is for the entire power plant.
o See Appendix B for maintenance intervals and costs

## Genset Capital Costs
Rated Power (kW) | IES ($) | Bill Stamm ($) | Unit Cost ($/kW)
180 | 74000 |  | 411.1111
370 | 152000 |  | 410.8108
500 |  | 205000 | 410
750 |  | 290000 | 386.6667
Genorator relplcement every 60,000-100,000 hours
Source: ACEP , "Diesel Generator Technology Report"
o CAPEX values are for a diesel plant, not just the diesel generator
o OPEX values (modeled) assume 55% load factor. These are for the generator only. The RCA data is for the entire power plant.
o See Appendix B for maintenance intervals and costs

## Assumptions
Assumptions
Horizon (years) | 25
Nominal Discount Rate | 3%
Load Inflation Rate | 1%
Fuel Cost Adjustment | 1 |  | https://www.commerce.alaska.gov/dcra/DCRAExternal/Community/Details/c7c0d5ad-dab5-40d3-bfd2-abd8a8969c17 | http://model-results.akenergyinventory.org/m0.24.6_d0.24.0/Shungnak/financial_and_demographic.html | https://akenergygateway.alaska.edu/community-data-summary/1413983/#history
Heating fuel cost ($/gal) | 7.99 |  | Accessed 8/1/2017 | Accessed 8/1/2017 | Accessed 8/1/2017
Diesel oil cost ($/gal) | 7.1633 |  | Alaska DOC | Alaska Affordable Energy Model Database (BETA) | AHFC/DCRA Survey: No. 1 Fuel Oil
HHV (Btu/gallon) | 134000 |  | 9 | 4.07 | 8.42 | 7.1633 | Diesel Price
Conversion (kWh/Btu) | 0.00029307 |  | 9.18 | 6.8 |  | 7.99 | Heating Fuel Price
Baseline total fuel use (gal/year) | 186075.5898
Baseline Gen O&M net present cost | -2655676.211
Baseline diesel fuel net present cost | -13815874.8773
Baseline heating fuel net present cost | -6752037.5899
Baseline total net present cost | 21141875662.7895
Energy Efficiency Cost Electrical Curve | 0.1493
Energy Efficiency Cost Electrical Curve | -0.9009
Energy Efficiency Cost Electrical Curve | 16.515
Energy Efficiency Cost Thermal Curve | 0.1123
Energy Efficiency Cost Thermal Curve | -0.6774
Energy Efficiency Cost Thermal Curve | 12.418
Baseline electrical load (kWh/year) | 1747196.0752
Baseline thermal load (kWh/year) | 2813162.6652
Assumed replacement usage (hours) | 80000
Gen replacement curve ($/kW) | 410.53
Gen replacement curve ($) | 105.26
202kW Gen O&M | 15.7808
314kW Gen O&M | 16.4528
365kW Gen O&M | 16.7588
397kW Gen O&M | 17.1422
Wind Replacement cost (First turbine) | 560000
Wind O&M Cost ($/year) | 17500 | (excludes repairs & replacements)
Solar O&M Cost ($/hour/100kW) | 0.54 | (excludes repairs & replacements)

## Low-EE Detailed
Summary Results
New Solar | No Generator | SG 200 | SG 300 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 500 | SG 200 | SG 200 | SG 300 | SG 500 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | WG 100 | WG 100 | WG 200 | WG 500 | WG 500 | WG 500 | WG 400 | WG 500
New Storage | No Battery | No Battery | No Battery | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery | No Battery | No Battery
New Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel
Energy Efficiency Cost | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013
Renewable Energy Purchase Cost | 0 | -1050000 | -1550000 | -1670000 | -2500000 | -2550000 | -2670000 | -3500000 | -3620000 | -4200000 | -4800000 | -4920000 | -5300000 | -5600000 | -6300000
Stove Purchase Cost | 0 | -10120.71 | -11406.3 | -11406.3 | -12622.45 | -16998.34 | -16998.34 | -19171.26 | -19156.47 | -22066.26 | -31875.59 | -31888.05 | -36018.14 | -34080.02 | -44837.12
New Generator Purchase Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Net Reduction in Imported Fuel | 12.1% | 17.97% | 20.68% | 20.73% | 29.38% | 25.12% | 25.16% | 33.44% | 33.27% | 40.96% | 58.24% | 58.1% | 60.29% | 56.82% | 62.98%
Marginal NPV (Utility Only) | 322318.1437 | -164377.1298 | -452984.8626 | -541591.706 | 720645.1291 | -1506307.498 | -1648045.0086 | -458558.9132 | -637142.2445 | 268383.3429 | 4091239.8088 | 3930330.4386 | 3462674.7782 | 1742434.1297 | 1841574.3456
Marginal NPV (Heating Customers Only) | 1477344.0172 | 1348719.8475 | 1353448.9965 | 1353465.671 | 1225557.679 | 1569130.2716 | 1569185.0593 | 1503304.7384 | 1507394.0674 | 1477089.2256 | 1581892.2361 | 1591911.8843 | 1771450.4847 | 1755720.7555 | 2222556.5619
Total Marginal NPV | 1799662.1609 | 1184342.7177 | 900464.1339 | 811873.965 | 1946202.8081 | 62822.7736 | -78859.9493 | 1044745.8253 | 870251.823 | 1745472.5685 | 5673132.0448 | 5522242.3229 | 5234125.2629 | 3498154.8852 | 4064130.9075
Total % ROI | 447.1% | 175% | 143.3% | 136.9% | 164.2% | 102% | 97.54% | 125.9% | 120.9% | 136.8% | 206% | 200.9% | 189.4% | 156.9% | 159.2%
Total Capital Cost | 518433.4013 | 1578554.1113 | 2079839.7013 | 2199839.7013 | 3031055.8513 | 3085431.7413 | 3205431.7413 | 4037604.6613 | 4157589.8713 | 4781657.9213 | 5391467.2513 | 5511479.7113 | 5895609.8013 | 6193671.6813 | 6904428.7813
Raw DATA
Simulation Statistics | 1 | 2 | 3 | 5 | 6 | 7 | 8 | 9 | 11 | 12 | 13 | 14 | 15 | 17 | 18
Total Sim Time | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000
Power Utility Statistics
Failure Statistics
Occurrences
Downtime (hrs)
Min | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000
Max | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000
Average | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000
Total | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000 | 219000
Thermal Load Service
Overall
Overall Energy Availability | 25.1% | 23.18% | 22.2% | 22.2% | 19.24% | 20.97% | 20.97% | 18.18% | 18.26% | 15.42% | 9.037% | 9.181% | 8.58% | 9.917% | 8.34%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Load Served (kWh) | 13239997 | 12224503 | 11710269 | 11710405 | 10148591 | 11058396 | 11058844 | 9589602 | 9629178 | 8132157 | 4766681 | 4842714 | 4525712 | 5231091 | 4399053
Total Load Not Served | 39506802 | 40522296 | 41036530 | 41036394 | 42598208 | 41688403 | 41687955 | 43157197 | 43117621 | 44614642 | 47980118 | 47904085 | 48221087 | 47515708 | 48347746
Post-Startup
Post-Startup Energy Availability
DBT Occurrences w/ Post-Startup Load Loss
Total Post-Startup Load Served (kWh) | 13239997 | 12224503 | 11710269 | 11710405 | 10148591 | 11058396 | 11058844 | 9589602 | 9629178 | 8132157 | 4766681 | 4842714 | 4525712 | 5231091 | 4399053
Total Post-Startup Load Not Served | 39506802 | 40522296 | 41036530 | 41036394 | 42598208 | 41688403 | 41687955 | 43157197 | 43117621 | 44614642 | 47980118 | 47904085 | 48221087 | 47515708 | 48347746
Variable Selections
New Solar | No Generator | SG 200 | SG 300 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 500 | SG 200 | SG 200 | SG 300 | SG 500 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | WG 100 | WG 100 | WG 200 | WG 500 | WG 500 | WG 500 | WG 400 | WG 500
New Storage | No Battery | No Battery | No Battery | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery | No Battery | No Battery
Metric Values
Purchase Cost | 0 | 1060120.71 | 1561406.3 | 1681406.3 | 2512622.45 | 2566998.34 | 2686998.34 | 3519171.26 | 3639156.47 | 4222066.26 | 4831875.59 | 4951888.05 | 5336018.14 | 5634080.02 | 6344837.12
Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Diesel Fuel Used (Gal/Hour) | 14.1 | 12.74 | 12.17 | 12.16 | 10.2 | 11.44 | 11.43 | 9.61 | 9.65 | 7.99 | 4.43 | 4.47 | 4.18 | 4.9 | 4.05
Heating Fuel Deferred (GHFE/Year) | 13684.74 | 12689.78 | 12740.28 | 12740.42 | 11676.71 | 14598.1 | 14598.56 | 14063.67 | 14097.88 | 13867.87 | 14830.16 | 14914.39 | 16456.48 | 16308.14 | 20318.03
Average Renewable Energy Spilled | 0 | 52871.43 | 615958.9 | 615958.9 | 1148633.88 | 3065274.41 | 3065274.41 | 4017013.04 | 4010532.05 | 5285022.56 | 9581507.86 | 9586965.61 | 11395945.6 | 10547049.03 | 15258659.62
Diesel Utilization | 0.5867 | 0.5249 | 0.4935 | 0.4939 | 0.4101 | 0.461 | 0.4615 | 0.384 | 0.3865 | 0.2969 | 0.1629 | 0.1653 | 0.1515 | 0.1761 | 0.1472
Heating Fuel Deferred from Waste Heat (GHFE/Year) | 13485.5987 | 12451.2673 | 11927.4943 | 11927.6328 | 10336.8472 | 11263.5291 | 11263.9854 | 9767.489 | 9807.7991 | 8283.0084 | 4855.1029 | 4932.5463 | 4609.6639 | 5328.1277 | 4480.6554
Heating Fuel Deferred from Stoves (GHFE/Year) | 199.1413 | 238.5127 | 812.7857 | 812.7872 | 1339.8628 | 3334.5709 | 3334.5746 | 4296.181 | 4290.0809 | 5584.8616 | 9975.0571 | 9981.8437 | 11846.8161 | 10980.0123 | 15837.3746
Cost
Fixed Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Cost | 0 | 1050000 | 1550000 | 1670000 | 2500000 | 2550000 | 2670000 | 3500000 | 3620000 | 4200000 | 4800000 | 4920000 | 5300000 | 5600000 | 6300000
Total Cost | 0 | 1050000 | 1550000 | 1670000 | 2500000 | 2550000 | 2670000 | 3500000 | 3620000 | 4200000 | 4800000 | 4920000 | 5300000 | 5600000 | 6300000
Generation
Total Diesel Generation | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278
Total Solar Generation | 0 | 0 | 300 | 300 | 300 | 500 | 500 | 500 | 500 | 500 | 200 | 200 | 300 | 500 | 500
Total Wind Generation | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 200 | 500 | 500 | 500 | 400 | 500
Overall Diesel Efficiency | 34.96% | 32.71% | 30.93% | 30.91% | 28.45% | 28.8% | 28.79% | 26.45% | 26.53% | 23.1% | 12.59% | 12.7% | 11.7% | 13.9% | 11.22%
Overall Diesel Utilization (%loading) | 58.67% | 52.49% | 49.35% | 49.39% | 41.01% | 46.1% | 46.15% | 38.4% | 38.65% | 29.69% | 16.29% | 16.53% | 15.15% | 17.61% | 14.72%
Solar Generated (kWh/25y)
Min | 0 | 4469315.17 | 6167321 | 6167321 | 6167321 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 4469315.17 | 4469315.17 | 6167321 | 8240192.09 | 8240192.09
Max | 0 | 4469315.17 | 6167321 | 6167321 | 6167321 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 4469315.17 | 4469315.17 | 6167321 | 8240192.09 | 8240192.09
Average | 0 | 4469315.17 | 6167321 | 6167321 | 6167321 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 4469315.17 | 4469315.17 | 6167321 | 8240192.09 | 8240192.09
Total | 0 | 4469315.17 | 6167321 | 6167321 | 6167321 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 4469315.17 | 4469315.17 | 6167321 | 8240192.09 | 8240192.09
Solar Spilled
Min | 0 | 52871.43 | 615958.9 | 615958.9 | 615958.9 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 52871.43 | 52871.43 | 615958.9 | 3065274.41 | 3065274.41
Max | 0 | 52871.43 | 615958.9 | 615958.9 | 615958.9 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 52871.43 | 52871.43 | 615958.9 | 3065274.41 | 3065274.41
Average | 0 | 52871.43 | 615958.9 | 615958.9 | 615958.9 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 52871.43 | 52871.43 | 615958.9 | 3065274.41 | 3065274.41
Total | 0 | 52871.43 | 615958.9 | 615958.9 | 615958.9 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 52871.43 | 52871.43 | 615958.9 | 3065274.41 | 3065274.41
Wind Generated
Min | 0 | 0 | 0 | 0 | 6390328.34 | 0 | 0 | 5923778.42 | 5787816.13 | 11392049.35 | 24970771.87 | 24828465.98 | 23920105.33 | 20001910.94 | 22144393.28
Max | 0 | 0 | 0 | 0 | 6390328.34 | 0 | 0 | 5923778.42 | 5787816.13 | 11392049.35 | 24970771.87 | 24828465.98 | 23920105.33 | 20001910.94 | 22144393.28
Average | 0 | 0 | 0 | 0 | 6390328.34 | 0 | 0 | 5923778.42 | 5787816.13 | 11392049.35 | 24970771.87 | 24828465.98 | 23920105.33 | 20001910.94 | 22144393.28
Total | 0 | 0 | 0 | 0 | 6390328.34 | 0 | 0 | 5923778.42 | 5787816.13 | 11392049.35 | 24970771.87 | 24828465.98 | 23920105.33 | 20001910.94 | 22144393.28
Wind Spilled
Min | 0 | 0 | 0 | 0 | 532674.98 | 0 | 0 | 951738.64 | 945257.64 | 2219748.16 | 9528636.44 | 9534094.18 | 10779986.7 | 7481774.62 | 12193385.21
Max | 0 | 0 | 0 | 0 | 532674.98 | 0 | 0 | 951738.64 | 945257.64 | 2219748.16 | 9528636.44 | 9534094.18 | 10779986.7 | 7481774.62 | 12193385.21
Average | 0 | 0 | 0 | 0 | 532674.98 | 0 | 0 | 951738.64 | 945257.64 | 2219748.16 | 9528636.44 | 9534094.18 | 10779986.7 | 7481774.62 | 12193385.21
Total | 0 | 0 | 0 | 0 | 532674.98 | 0 | 0 | 951738.64 | 945257.64 | 2219748.16 | 9528636.44 | 9534094.18 | 10779986.7 | 7481774.62 | 12193385.21
Weight
Fixed Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Volume
Fixed Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Min | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Average | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48 | 189.48
Max | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49 | 379.49
Tier (Only)
Load Service
Priority
Overall
Overall Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Load Served (kWh) | 41495904.13 | 41495902.79 | 41495902.2 | 41495912.83 | 41495895.52 | 41495915.79 | 41495909.36 | 41495899.56 | 41495921.53 | 41495895.19 | 41495917.06 | 41495932.18 | 41495907.78 | 41495913.12 | 41495917.64
Total Load Not Served | 31.25 | 32.59 | 33.18 | 22.55 | 39.86 | 19.59 | 26.02 | 35.81 | 13.85 | 40.19 | 18.32 | 3.2 | 27.6 | 22.26 | 17.74
Post-Startup
Post-Startup Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DBT Occurrences w/ Post-Startup Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Post-Startup Load Served | 41495904.13 | 41495902.79 | 41495902.2 | 41495909.04 | 41495892.44 | 41495915.79 | 41495905.56 | 41495896.49 | 41495917.63 | 41495891.94 | 41495913.43 | 41495927.86 | 41495904.16 | 41495909.6 | 41495914.01
Total Post-Startup Load Not Served | 30.56 | 31.9 | 32.49 | 21.52 | 38.12 | 18.9 | 24.99 | 34.07 | 12.93 | 38.62 | 17.12 | 2.7 | 26.4 | 20.95 | 16.54
Startup Time
Min | 0.17 | 0.17 | 0.17 | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Max | 0.17 | 0.17 | 0.17 | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Average | 0.17 | 0.17 | 0.17 | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Renewable Penetration
Min | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Max | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Average | 0% | 14.81% | 20.1% | 20.1% | 35.85% | 26.22% | 26.22% | 40.44% | 40.12% | 53.37% | 74.48% | 74.23% | 76.19% | 72.61% | 77.21%
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 0.00% | 0% | 50.9% | 50.9% | 50.9% | 4.3% | 50.9% | 50.9% | 4.26% | 5.54% | 4.77% | 4.18% | 4.64% | 3.71% | 4.35% | 4.69%
<= 25.00% | 0% | 27.61% | 22.62% | 22.62% | 44.4% | 17.13% | 17.13% | 41.92% | 41.1% | 18.49% | 11.8% | 11.72% | 11.04% | 11.38% | 10%
<= 50.00% | 0% | 9.65% | 8.72% | 8.72% | 26.67% | 7.85% | 7.85% | 23.57% | 23.2% | 27.09% | 8.2% | 8.07% | 7.66% | 9.02% | 6.77%
<= 75.00% | 0% | 6.36% | 5.92% | 5.92% | 8.32% | 4.96% | 4.96% | 7.45% | 7.4% | 19.08% | 10.66% | 10.54% | 10.21% | 13.87% | 9.17%
<= 100.00% | 0% | 5.48% | 11.84% | 11.84% | 16.3% | 19.16% | 19.16% | 22.81% | 22.76% | 30.56% | 65.16% | 65.03% | 67.38% | 61.37% | 69.37%
<= 110.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 120.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 130.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 140.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Diesel Fuel Use
Min | 3087479.67 | 2790964.56 | 2664262.91 | 2663719.5 | 2233778.06 | 2504280.17 | 2502493.36 | 2104093.77 | 2113095.86 | 1750692.15 | 969335.36 | 979424.46 | 915986.95 | 1072501.99 | 887808.47
Max | 3087479.67 | 2790964.56 | 2664262.91 | 2663719.5 | 2233778.06 | 2504280.17 | 2502493.36 | 2104093.77 | 2113095.86 | 1750692.15 | 969335.36 | 979424.46 | 915986.95 | 1072501.99 | 887808.47
Average | 3087479.67 | 2790964.56 | 2664262.91 | 2663719.5 | 2233778.06 | 2504280.17 | 2502493.36 | 2104093.77 | 2113095.86 | 1750692.15 | 969335.36 | 979424.46 | 915986.95 | 1072501.99 | 887808.47
Natural Gas Use
Min | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Max | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Average | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Spinning Reserve
Min | 2.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Max | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Average | 40.19% | 47.54% | 51.06% | 50.99% | 59.43% | 54.71% | 54.67% | 62.11% | 61.93% | 71.12% | 84.57% | 84.43% | 85.39% | 83.12% | 85.99%
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 0.00% | 0% | 0% | 0% | 0% | 0% | 0.03% | 0.01% | 0.01% | 0.02% | 0.03% | 0.01% | 0.02% | 0.07% | 0.06% | 0.06%
<= 5.00% | 0% | 0% | 0.01% | 0.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 10.00% | 0.07% | 0.09% | 0.08% | 0.08% | 0.02% | 0.07% | 0.06% | 0.02% | 0.02% | 0.01% | 0.01% | 0.01% | 0.01% | 0.01% | 0.01%
<= 15.00% | 0.47% | 0.48% | 0.39% | 0.39% | 0.1% | 0.35% | 0.34% | 0.1% | 0.11% | 0.07% | 0.05% | 0.05% | 0.02% | 0.03% | 0.02%
<= 20.00% | 3.37% | 2.85% | 2.54% | 2.56% | 0.78% | 2.34% | 2.36% | 0.78% | 0.81% | 0.41% | 0.2% | 0.25% | 0.19% | 0.23% | 0.21%
<= 25.00% | 6.94% | 5.72% | 4.91% | 5.02% | 1.67% | 4.67% | 4.83% | 1.73% | 1.8% | 1.06% | 0.64% | 0.69% | 0.67% | 0.75% | 0.73%
<= 30.00% | 9.9% | 8.12% | 7.21% | 7.41% | 2.99% | 6.87% | 7.08% | 3.03% | 3.11% | 1.88% | 1.2% | 1.22% | 1.32% | 1.46% | 1.35%
<= 40.00% | 24.08% | 20.13% | 19.01% | 19.03% | 11.27% | 18.01% | 18.03% | 10.9% | 11.17% | 5.34% | 3.69% | 3.68% | 3.88% | 4.33% | 3.92%
<= 50.00% | 35.11% | 25.28% | 24.61% | 24.25% | 21.16% | 22.62% | 22.17% | 19.75% | 19.88% | 9.01% | 5.58% | 5.68% | 4.76% | 5.05% | 4.75%
<= 75.00% | 20% | 26.88% | 24.9% | 24.94% | 39.67% | 22.24% | 22.3% | 35.64% | 35.13% | 39.98% | 15.56% | 15.54% | 14.19% | 16.78% | 12.95%
<= 100.00% | 0.04% | 10.45% | 16.34% | 16.32% | 22.33% | 22.79% | 22.82% | 28.04% | 27.95% | 42.22% | 73.06% | 72.85% | 74.88% | 71.31% | 76%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Diesel Gen Set Data
JD 6619 Run Time (hours/year) | 3298.1488 | 3694.8136 | 3597.4812 | 3570.9748 | 2863.5948 | 3496.7844 | 3377.0404 | 2864.9372 | 2847.514 | 2838.5084 | 3003.6788 | 3022.878 | 2844.5888 | 2870.3596 | 2881.5412
CAT 3406 Run Time (hours/year) | 7007.4184 | 6113.3472 | 6123.786 | 6044.3684 | 5290.678 | 6300.4564 | 6168.722 | 5174.8396 | 5333.4508 | 4671.0544 | 4690.954 | 4745.5728 | 4480.9828 | 4469.492 | 4417.288
SD 60 Run Time (hours/year) | 860.0236 | 1087.178 | 974.1636 | 994.2228 | 1418.1344 | 880.3592 | 1218.6596 | 1509.8768 | 1433.7012 | 1922.0816 | 1926.4496 | 1827.662 | 2148.33 | 2143.976 | 2167.3308
CMS K19G2 Run Time (hours/year) | 25.4304 | 40.8404 | 17.126 | 18.5996 | 31.5956 | 4.388 | 13.5604 | 6.886 | 20.8084 | 269.3676 | 214.3516 | 254.2588 | 269.1484 | 272.866 | 275.3796
Total Run Time | 11191.0212 | 10936.1792 | 10712.5568 | 10628.1656 | 9604.0028 | 10681.988 | 10777.9824 | 9556.5396 | 9635.4744 | 9701.012 | 9835.434 | 9850.3716 | 9743.05 | 9756.6936 | 9741.5396
JD 6619 Run Time (hours) | 82453.72 | 92370.34 | 89937.03 | 89274.37 | 71589.87 | 87419.61 | 84426.01 | 71623.43 | 71187.85 | 70962.71 | 75091.97 | 75571.95 | 71114.72 | 71758.99 | 72038.53
CAT 3406 Run Time (hours) | 175185.46 | 152833.68 | 153094.65 | 151109.21 | 132266.95 | 157511.41 | 154218.05 | 129370.99 | 133336.27 | 116776.36 | 117273.85 | 118639.32 | 112024.57 | 111737.3 | 110432.2
SD 60 Run Time (hours) | 21500.59 | 27179.45 | 24354.09 | 24855.57 | 35453.36 | 22008.98 | 30466.49 | 37746.92 | 35842.53 | 48052.04 | 48161.24 | 45691.55 | 53708.25 | 53599.4 | 54183.27
CMS K19G2 Run Time (hours) | 635.76 | 1021.01 | 428.15 | 464.99 | 789.89 | 109.7 | 339.01 | 172.15 | 520.21 | 6734.19 | 5358.79 | 6356.47 | 6728.71 | 6821.65 | 6884.49
Total Run Time | 279775.53 | 273404.48 | 267813.92 | 265704.14 | 240100.07 | 267049.7 | 269449.56 | 238913.49 | 240886.86 | 242525.3 | 245885.85 | 246259.29 | 243576.25 | 243917.34 | 243538.49
Assumptions
Horizon (years) | 25
Nominal Discount Rate | 3%
Load Inflation Rate | 1%
Fuel Cost Adjustment | 1
Heating fuel cost ($/gal) | 7.99
Diesel oil cost ($/gal) | 7.1633
HHV (Btu/gallon) | 134000
Conversion (kWh/Btu) | 0.00029307
Baseline total fuel use (gal/year) | 186075.5898
Baseline Gen O&M net present cost | -2655676.211
Baseline diesel fuel net present cost | -13815874.8773
Baseline heating fuel net present cost | -6752037.5899
Baseline total net present cost | 21141875662.7895
Energy Efficiency Cost Electrical Curve | 0.1493
Energy Efficiency Cost Electrical Curve | -0.9009
Energy Efficiency Cost Electrical Curve | 16.515
Energy Efficiency Cost Thermal Curve | 0.1123
Energy Efficiency Cost Thermal Curve | -0.6774
Energy Efficiency Cost Thermal Curve | 12.418
Baseline electrical load (kWh/year) | 1747196.0752
Baseline thermal load (kWh/year) | 2813162.6652
EE electrical load(kWh/year) | 1659836.1652
EE thermal load(kWh/year) | 2109871.96
Assumed replacement usage (hours) | 80000
Gen replacement curve ($/kW) | 410.53
Gen replacement curve ($) | 105.26
202kW Gen O&M | 15.7808
314kW Gen O&M | 16.4528
365kW Gen O&M | 16.7588
397kW Gen O&M | 17.1422
Wind Replacement cost (First turbine) | 560000
Wind O&M Cost ($/kWh) | 17500
Solar O&M Cost ($/hour/100kW) | 0.54
1.0379
EE electrical load reduction (%) | 0.05 |  | 1.6126
EE thermal load reduction (%) | 0.25 |  | 1.8744
1.9462
EE electrical load reduction cost ($/kWh/year) | 0.14554
EE thermal load reduction cost ($/kWh/year) | 0.71908
EE electrical load reduction cost ($/kWh/year) | -12714.5837
EE thermal load reduction cost ($/kWh/year) | -505718.8176 | -518433.4013
Financial calculations
RE Purchase Cost | 0 | -1050000 | -1550000 | -1670000 | -2500000 | -2550000 | -2670000 | -3500000 | -3620000 | -4200000 | -4800000 | -4920000 | -5300000 | -5600000 | -6300000
Stove Cost | 0 | -10120.71 | -11406.3 | -11406.3 | -12622.45 | -16998.34 | -16998.34 | -19171.26 | -19156.47 | -22066.26 | -31875.59 | -31888.05 | -36018.14 | -34080.02 | -44837.12
kW of Stoves | 0 | 0.24142 | 2.8126 | 2.8126 | 5.2449 | 13.9967 | 13.9967 | 18.3425 | 18.3129 | 24.1325 | 43.7512 | 43.7761 | 52.0363 | 48.16 | 69.6742
# of Stoves | 0 | 1 | 1 | 1 | 1 | 3 | 3 | 4 | 4 | 5 | 8 | 8 | 9 | 9 | 12
Gen Replacement Cost (per year)
JD 6619 | -3423.1618 | -3834.8618 | -3733.8401 | -3706.329 | -2972.1365 | -3629.3265 | -3505.0437 | -2973.5298 | -2955.4462 | -2946.0992 | -3117.5302 | -3137.4572 | -2952.4101 | -2979.1577 | -2990.7631
CAT 3406 | -11300.4853 | -9858.6649 | -9875.499 | -9747.4265 | -8531.9907 | -10160.4058 | -9947.9649 | -8345.1844 | -8600.9681 | -7532.7572 | -7564.8482 | -7652.929 | -7226.239 | -7207.7084 | -7123.5218
SD 60 | -1611.9929 | -2037.7617 | -1825.9322 | -1863.5303 | -2658.0928 | -1650.1091 | -2284.2054 | -2830.051 | -2687.2706 | -3602.6707 | -3610.8579 | -3425.6945 | -4026.7414 | -4018.5804 | -4062.3557
CMS | -51.8417 | -83.256 | -34.9126 | -37.9166 | -64.4099 | -8.9452 | -27.6438 | -14.0376 | -42.4194 | -549.1249 | -436.9709 | -518.3246 | -548.6781 | -556.2567 | -561.3808
New Small (100kW) Gen (purchase) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Gen O&M Cost (per year)
JD 6619 | -52047.2617 | -58306.9297 | -56770.9514 | -56352.6606 | -45189.6736 | -55181.8804 | -53292.2303 | -45210.8577 | -44935.9066 | -44793.7914 | -47400.3042 | -47703.282 | -44889.7447 | -45296.4273 | -45472.8813
CAT 3406 | -115291.3031 | -100581.3731 | -100753.1201 | -99446.4822 | -87046.2025 | -103659.834 | -101492.4409 | -85140.3422 | -87749.9326 | -76851.6903 | -77179.0934 | -78077.7229 | -73724.4898 | -73535.4345 | -72676.5351
SD 60 | -14412.9205 | -18219.7443 | -16325.7642 | -16661.9313 | -23766.1599 | -14753.7197 | -20423.2116 | -25303.6478 | -24027.04 | -32211.685 | -32284.8872 | -30629.3305 | -36003.3254 | -35930.3578 | -36321.755
CMS | -435.9341 | -700.0961 | -293.5781 | -318.8389 | -541.6195 | -75.2202 | -232.4557 | -118.0415 | -356.7027 | -4617.5653 | -3674.4676 | -4358.5665 | -4613.8077 | -4677.5357 | -4720.6245
Deasil Fuel use (Gal/year) | 123516 | 111602.4 | 106609.2 | 106521.6 | 89352 | 100214.4 | 100126.8 | 84183.6 | 84534 | 69992.4 | 38806.8 | 39157.2 | 36616.8 | 42924 | 35478
Heating Fuel use (Gal/year) | 40040.5113 | 41035.4713 | 40984.9713 | 40984.8313 | 42048.5413 | 39127.1513 | 39126.6913 | 39661.5813 | 39627.3713 | 39857.3813 | 38895.0913 | 38810.8613 | 37268.7713 | 37417.1113 | 33407.2213
Total Fuel usage (Gal/year) | 163556.5113 | 152637.8713 | 147594.1713 | 147506.4313 | 131400.5413 | 139341.5513 | 139253.4913 | 123845.1813 | 124161.3713 | 109849.7813 | 77701.8913 | 77968.0613 | 73885.5713 | 80341.1113 | 68885.2213
New Wind Turbines (#) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 5 | 5 | 5 | 4 | 5
New 100kW Solar Fields (#) | 0 | 2 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 3 | 5 | 5
Wind Replacement Cost (per replacement) | 0 | 0 | 0 | 0 | -560000 | 0 | 0 | -560000 | -560000 | -1092000 | -2520000 | -2520000 | -2520000 | -2072000 | -2520000
Wind Replacement NPV (Turbines are replaced every 20 years: this means that the first replacement is out of the time horizon for this analysis and so the replacement cost is not used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Replacement NPV (converter only after 10 years) | 0 | -126423.7234 | -189635.5851 | -189635.5851 | -189635.5851 | -316059.3085 | -316059.3085 | -316059.3085 | -316059.3085 | -316059.3085 | -126423.7234 | -126423.7234 | -189635.5851 | -316059.3085 | -316059.3085
Wind O&M Cost per year ($/year) | 0 | -34562.5 | -51187.5 | -51187.5 | -51187.5 | -83125 | -83125 | -83125 | -83125 | -83125 | -34562.5 | -34562.5 | -51187.5 | -83125 | -83125
Solar O&M Cost per year ($/year) | 0 | -9460.8 | -14191.2 | -14191.2 | -14191.2 | -23652 | -23652 | -23652 | -23652 | -23652 | -9460.8 | -9460.8 | -14191.2 | -23652 | -23652
Gen + Wind + Solar O&M + Genorator Replacement Cost
Year
1 | -198574.901 | -237645.9878 | -254992.2977 | -253513.8155 | -236148.9854 | -295896.441 | -297982.1963 | -276712.692 | -278132.6861 | -279882.3841 | -219292.2597 | -219526.6072 | -239364.1361 | -280978.4585 | -280706.8174
2 | -187175.8894 | -224004.1359 | -240354.6967 | -238961.0854 | -222593.0675 | -278910.7748 | -280876.7992 | -260828.2515 | -262166.7321 | -263815.9903 | -206703.9869 | -206924.8819 | -225623.6555 | -264849.1455 | -264593.0978
3 | -181724.1644 | -217479.7436 | -233354.0745 | -232001.0538 | -216109.7743 | -270787.16 | -272695.9216 | -253231.3121 | -254530.8079 | -256132.0294 | -200683.4824 | -200897.9436 | -219052.0927 | -257135.0927 | -256886.5027
4 | -176431.2276 | -211145.3822 | -226557.3539 | -225243.7415 | -209815.3149 | -262900.1554 | -264753.3219 | -245855.6428 | -247117.2892 | -248671.8732 | -194838.3325 | -195046.5472 | -212671.9347 | -249645.7211 | -249404.3716
5 | -171292.454 | -204995.5167 | -219958.596 | -218683.2442 | -203704.1892 | -255242.8693 | -257042.0601 | -238694.7989 | -239919.6983 | -241429.0031 | -189163.4296 | -189365.5798 | -206477.6065 | -242374.4865 | -242140.1666
6 | -166303.3534 | -199024.7734 | -213552.0349 | -212313.8293 | -197771.0575 | -247808.611 | -249555.3982 | -231742.5232 | -232931.7459 | -234397.0904 | -183653.8151 | -183850.0774 | -200463.6956 | -235315.0354 | -235087.5404
7 | -161459.5664 | -193227.9354 | -207332.0728 | -206129.9314 | -192010.7354 | -240590.8844 | -242286.7944 | -224992.741 | -226147.3261 | -227569.9907 | -178304.6749 | -178495.2208 | -194624.9472 | -228461.1995 | -228240.3304
8 | -156756.8606 | -187599.9373 | -201293.2745 | -200126.147 | -186418.1897 | -233583.3829 | -235229.8974 | -218439.5543 | -219560.5108 | -220941.7385 | -173111.3348 | -173296.3309 | -188956.2594 | -221806.9898 | -221592.5538
9 | -152191.1268 | -182135.8614 | -195430.3636 | -194297.2301 | -180988.5337 | -226779.9834 | -228378.5412 | -212077.2372 | -213165.5444 | -214506.5422 | -168069.2571 | -168248.8649 | -183452.6791 | -215346.592 | -215138.4018
10 | -147758.3755 | -176830.9334 | -189738.2171 | -188638.0875 | -175717.023 | -220174.7412 | -221726.739 | -205900.2303 | -206956.8393 | -208258.7789 | -163174.036 | -163348.4126 | -178109.3971 | -209074.3612 | -208872.2347
11 | -143454.7335 | -171680.5179 | -184211.8613 | -183143.7742 | -170599.0515 | -213761.8847 | -215268.6787 | -199903.1362 | -200928.9702 | -202192.9892 | -158421.3942 | -158590.6918 | -172921.7448 | -202984.8167 | -202788.5774
12 | -139276.4403 | -166680.1145 | -178846.4672 | -177809.4895 | -165630.1471 | -207535.8104 | -208998.7172 | -194080.7148 | -195076.6701 | -196303.873 | -153807.1788 | -153971.5455 | -167885.1891 | -197072.6375 | -196882.114
13 | -135219.8449 | -161825.3538 | -173637.3468 | -172630.5724 | -160805.968 | -201491.078 | -202911.3759 | -188427.8784 | -189394.8253 | -190586.2845 | -149327.3581 | -149486.9373 | -162995.3292 | -191332.6578 | -191147.6835
14 | -131281.4029 | -157111.994 | -168579.9484 | -167602.4974 | -156122.299 | -195622.4058 | -197001.3358 | -182939.6878 | -183878.4712 | -185035.2276 | -144978.0176 | -145132.9489 | -158247.8925 | -185759.862 | -185580.2752
15 | -127457.6727 | -152535.9165 | -163669.8528 | -162720.8713 | -151575.0476 | -189924.6659 | -191263.4328 | -177611.3474 | -178522.7875 | -179645.8521 | -140755.3569 | -140905.7756 | -153638.7306 | -180349.3805 | -180175.0245
16 | -123745.3133 | -148093.1228 | -158902.7697 | -157981.4285 | -147160.2404 | -184392.8795 | -185692.6532 | -172438.2013 | -173323.0947 | -174413.4486 | -136655.6863 | -136801.7239 | -149163.8161 | -175096.486 | -174927.2082
17 | -120141.0809 | -143779.7309 | -154274.5337 | -153380.0276 | -142874.0198 | -179022.2131 | -180284.1293 | -167415.7294 | -168274.8492 | -169333.4453 | -132675.4236 | -132817.2077 | -144819.2389 | -169996.5883 | -169832.241
18 | -116641.8261 | -139591.9718 | -149781.1007 | -148912.6482 | -138712.6406 | -173807.9739 | -175033.1353 | -162539.5431 | -163373.64 | -164401.4032 | -128811.0908 | -128948.7453 | -140601.2028 | -165045.2314 | -164885.6709
19 | -113244.4913 | -135526.1862 | -145418.5444 | -144575.3866 | -134672.4666 | -168745.6057 | -169935.0828 | -157805.3817 | -158615.1845 | -159613.0128 | -125059.3115 | -125192.9566 | -136506.0222 | -160238.0887 | -160083.1756
20 | -109946.1081 | -131578.8215 | -141183.0528 | -140364.453 | -130749.9676 | -163830.6851 | -164985.5173 | -153209.1084 | -153995.3247 | -154964.0901 | -121416.8073 | -121546.5598 | -132530.1186 | -155570.9599 | -155420.5589
Total Gen O&M + Replacement Cost | -2960076.8329 | -3542493.937 | -3801068.4595 | -3779029.3143 | -3520178.7188 | -4410810.2056 | -4441901.7276 | -4124845.7119 | -4146012.9975 | -4213253.307 | -3310060.4941 | -3313553.8186 | -3609263.9487 | -4229592.0511 | -4225542.8064
Diesel Fuel Cost
Year
1 | -884786.28 | -799445.192 | -763677.236 | -763049.728 | -640058.16 | -717869.152 | -717241.644 | -603035.188 | -605545.22 | -501378.892 | -277986.044 | -280496.076 | -262298.344 | -307478.92 | -254140.74
2 | -833995.928 | -753553.7676 | -719839.0386 | -719247.5521 | -603316.2032 | -676660.526 | -676069.0395 | -568418.5013 | -570784.4472 | -472597.6925 | -262028.5079 | -264394.4538 | -247241.346 | -289828.3721 | -239552.0219
3 | -809704.7845 | -731605.5996 | -698872.853 | -698298.5943 | -585743.8866 | -656951.967 | -656377.7082 | -551862.6226 | -554159.6574 | -458832.7112 | -254396.6096 | -256693.6444 | -240040.1418 | -281386.7691 | -232574.7785
4 | -786121.15 | -710296.6986 | -678517.333 | -677959.8002 | -568683.3851 | -637817.4437 | -637259.9109 | -535788.954 | -538019.0849 | -445468.6516 | -246986.9996 | -249217.1305 | -233048.6813 | -273191.0379 | -225800.7558
5 | -763224.4174 | -689608.4453 | -658754.6922 | -658213.3983 | -552119.7913 | -619240.2366 | -618698.9426 | -520183.4505 | -522348.6261 | -432493.8365 | -239793.2035 | -241958.3791 | -226260.8557 | -265234.0174 | -219224.0348
6 | -740994.58 | -669522.7624 | -639567.6623 | -639042.1343 | -536038.6324 | -601204.1132 | -600678.5851 | -505032.4762 | -507134.5885 | -419896.9287 | -232808.9354 | -234911.0477 | -219670.7337 | -257508.7548 | -212838.8687
7 | -719412.2136 | -650022.0994 | -620939.478 | -620429.2566 | -520425.8567 | -583693.3137 | -583183.0923 | -490322.7924 | -492363.6781 | -407666.9211 | -226028.0926 | -228068.9784 | -213272.5569 | -250008.4998 | -206639.6784
8 | -698458.4598 | -631089.4169 | -602853.8621 | -602358.5015 | -505267.822 | -566692.5376 | -566197.177 | -476041.546 | -478022.9885 | -395793.1272 | -219444.7501 | -221426.1926 | -207060.7349 | -242726.6988 | -200621.047
9 | -678115.0095 | -612708.1717 | -585295.0118 | -584814.0791 | -490551.2835 | -550186.9297 | -549705.9971 | -462176.2583 | -464099.9888 | -384265.1721 | -213053.1555 | -214976.886 | -201029.8397 | -235656.9891 | -194777.7155
10 | -658364.0869 | -594862.3027 | -568247.5843 | -567780.6594 | -476263.382 | -534162.0677 | -533695.1428 | -448714.8139 | -450582.5134 | -373072.9826 | -206847.7238 | -208715.4233 | -195174.6017 | -228793.1933 | -189104.5782
11 | -639188.4339 | -577536.2162 | -551696.6837 | -551243.3586 | -462391.633 | -518603.9492 | -518150.6241 | -435645.4503 | -437458.7509 | -362206.7792 | -200823.0328 | -202636.3333 | -189489.9045 | -222129.3139 | -183596.6778
12 | -620571.2951 | -560714.773 | -535627.8483 | -535187.7268 | -448923.9156 | -503498.9798 | -503058.8583 | -422956.7479 | -424717.2339 | -351657.0672 | -194973.8182 | -196734.3042 | -183970.7811 | -215659.5281 | -178249.2018
13 | -602496.403 | -544383.2747 | -520027.0372 | -519599.7348 | -435848.4617 | -488833.961 | -488406.6586 | -410637.6193 | -412346.829 | -341414.6284 | -189294.9692 | -191004.1788 | -178612.4088 | -209378.1826 | -173057.4774
14 | -584947.9641 | -528527.4512 | -504880.6186 | -504465.7619 | -423153.8463 | -474596.0786 | -474181.2219 | -398677.3003 | -400336.7272 | -331470.513 | -183781.5235 | -185440.9503 | -173410.1057 | -203279.7889 | -168016.9684
15 | -567910.6447 | -513133.4478 | -490175.3579 | -489772.5844 | -410828.977 | -460772.8919 | -460370.1184 | -387065.3401 | -388676.4341 | -321816.032 | -178428.6636 | -180039.7576 | -168359.3259 | -197359.0184 | -163123.2703
16 | -551369.558 | -498187.8134 | -475898.4057 | -475507.3635 | -398863.0845 | -447352.3222 | -446961.28 | -375791.5923 | -377355.7613 | -312442.7495 | -173231.7122 | -174795.8811 | -163455.6562 | -191610.6975 | -158372.1071
17 | -535310.2505 | -483677.4887 | -462037.2871 | -461657.6344 | -387245.7131 | -434322.6429 | -433942.9903 | -364846.2062 | -366364.8168 | -303342.4753 | -168186.1283 | -169704.739 | -158694.8118 | -186029.8034 | -153759.3273
18 | -519718.6898 | -469589.7949 | -448579.8904 | -448211.2956 | -375966.7117 | -421672.4689 | -421303.874 | -354219.6176 | -355693.9969 | -294507.2575 | -163287.5032 | -164761.8825 | -154072.6329 | -180611.4596 | -149280.9003
19 | -504581.2522 | -455912.4222 | -435514.4567 | -435156.5976 | -365016.225 | -409390.7465 | -409032.8874 | -343902.5414 | -345333.9776 | -285929.3762 | -158531.5565 | -159962.9927 | -149585.0804 | -175350.9316 | -144932.9129
20 | -489884.7109 | -442633.4196 | -422829.5696 | -422482.1336 | -354384.6845 | -397466.7441 | -397119.3082 | -333885.9625 | -335275.7064 | -277601.3362 | -153914.1326 | -155303.8764 | -145228.2334 | -170243.6229 | -140711.5659
Total Diesel Fuel Cost | -13189156.1118 | -11917010.5577 | -11383831.9064 | -11374477.895 | -9541091.6553 | -10700989.0722 | -10691635.0608 | -8989204.9811 | -9026621.0268 | -7473855.13 | -4143827.0621 | -4181243.1078 | -3909976.7764 | -4583465.5991 | -3788374.6278
Heating Fuel Cost
Year
1 | -319923.6856 | -327873.416 | -327469.921 | -327468.8024 | -335967.8453 | -312625.9392 | -312622.2638 | -316896.0349 | -316622.697 | -318460.4769 | -310771.7798 | -310098.7821 | -297777.483 | -298962.7196 | -266923.6985
2 | -301558.7573 | -309052.1406 | -308671.8079 | -308670.7535 | -316681.9166 | -294679.9314 | -294676.4669 | -298704.9061 | -298447.2589 | -300179.5427 | -292932.2083 | -292297.8434 | -280683.8373 | -281801.0365 | -251601.1862
3 | -292775.4925 | -300050.622 | -299681.3669 | -299680.3432 | -307458.1714 | -286097.0207 | -286093.6572 | -290004.7632 | -289754.6203 | -291436.4492 | -284400.2022 | -283784.314 | -272508.5799 | -273593.2393 | -244272.9963
4 | -284248.051 | -291311.2835 | -290952.7834 | -290951.7895 | -298503.079 | -277764.0978 | -277760.8323 | -281558.0225 | -281315.1653 | -282948.009 | -276116.7012 | -275518.7514 | -264571.4368 | -265624.5042 | -237158.2489
5 | -275968.9815 | -282826.4888 | -282478.4305 | -282477.4655 | -289808.8146 | -269673.8814 | -269670.7109 | -273357.3034 | -273121.5197 | -274706.8048 | -268074.4672 | -267493.9334 | -256865.4726 | -257887.8681 | -230250.7271
6 | -267931.05 | -274588.8241 | -274250.9034 | -274249.9665 | -281367.7812 | -261819.3023 | -261816.2242 | -265395.4402 | -265166.524 | -266705.6358 | -260266.473 | -259702.848 | -249383.954 | -250376.571 | -223544.3952
7 | -260127.233 | -266591.0913 | -266263.013 | -266262.1034 | -273172.6031 | -254193.4974 | -254190.5089 | -257665.4759 | -257443.2272 | -258937.5104 | -252685.8961 | -252138.6874 | -242120.3437 | -243084.0495 | -217033.3934
8 | -252550.7117 | -258826.3023 | -258507.7796 | -258506.8965 | -265216.1195 | -246789.8033 | -246786.9019 | -250160.6562 | -249944.8808 | -251395.6412 | -245326.1127 | -244794.8421 | -235068.2948 | -236003.9315 | -210712.0324
9 | -245194.8657 | -251287.6721 | -250978.4268 | -250977.5695 | -257491.3781 | -239601.7507 | -239598.9339 | -242874.4235 | -242664.9328 | -244073.4381 | -238180.692 | -237664.8953 | -228221.6455 | -229130.0306 | -204574.7888
10 | -238053.2677 | -243968.6137 | -243668.3755 | -243667.5432 | -249991.6293 | -232623.059 | -232620.3241 | -235800.4112 | -235597.0221 | -236964.503 | -231243.3903 | -230742.6168 | -221574.4131 | -222456.3404 | -198616.2998
11 | -231119.6773 | -236862.7317 | -236571.2384 | -236570.4303 | -242710.3197 | -225847.6301 | -225844.9749 | -228932.4381 | -228734.9729 | -230062.6243 | -224508.1459 | -224021.958 | -215120.7894 | -215977.0295 | -192831.359
12 | -224388.0363 | -229963.8172 | -229680.8139 | -229680.0294 | -235641.0871 | -219269.5438 | -219266.9659 | -222264.503 | -222072.7893 | -223361.7711 | -217969.0737 | -217497.0466 | -208855.1353 | -209686.4364 | -187214.9117
13 | -217852.4624 | -223265.842 | -222991.0815 | -222990.3198 | -228777.7544 | -212883.0522 | -212880.5494 | -215790.7796 | -215604.6498 | -216856.0885 | -211620.4599 | -211162.1812 | -202771.9761 | -203579.0645 | -181762.0502
14 | -211507.245 | -216762.9534 | -216496.1956 | -216495.4561 | -222114.3247 | -206682.5749 | -206680.1451 | -209505.6112 | -209324.9027 | -210539.8917 | -205456.7572 | -205011.8264 | -196865.9962 | -197649.5772 | -176468.0099
15 | -205346.8398 | -210449.4693 | -210190.4812 | -210189.7632 | -215644.9754 | -200662.6941 | -200660.335 | -203403.5061 | -203228.0609 | -204407.6619 | -199472.5798 | -199040.6081 | -191132.0351 | -191892.7934 | -171328.1649
16 | -199365.8639 | -204319.8731 | -204068.4283 | -204067.7313 | -209364.0538 | -194818.1496 | -194815.8592 | -197479.1321 | -197308.797 | -198454.0406 | -193662.6988 | -193243.3089 | -185565.0826 | -186303.6829 | -166338.0242
17 | -193559.0912 | -198368.8088 | -198124.6877 | -198124.0109 | -203266.0717 | -189143.8346 | -189141.6109 | -191727.3127 | -191561.9388 | -192673.8259 | -188022.0377 | -187614.863 | -180160.2744 | -180877.362 | -161493.2274
18 | -187921.4478 | -192591.0765 | -192354.0657 | -192353.4087 | -197345.7006 | -183634.7909 | -183632.632 | -186143.0221 | -185982.4649 | -187061.9669 | -182545.6676 | -182150.3524 | -174912.8878 | -175609.0894 | -156789.5411
19 | -182448.0075 | -186981.6277 | -186751.5201 | -186750.8822 | -191597.7676 | -178286.2047 | -178284.1087 | -180721.3806 | -180565.4999 | -181613.5601 | -177228.8035 | -176845.0023 | -169818.3376 | -170494.2615 | -152222.8555
20 | -177133.9879 | -181535.5609 | -181312.1555 | -181311.5361 | -186017.2501 | -173093.4027 | -173091.3677 | -175457.6511 | -175306.3105 | -176323.8447 | -172066.7995 | -171694.177 | -164872.1725 | -165528.4092 | -147789.1801
Total Heating Fuel Cost | -4768974.755 | -4887478.2147 | -4881463.4757 | -4881446.8012 | -5008138.6432 | -4660190.1607 | -4660135.373 | -4723842.7738 | -4719768.2348 | -4747163.2866 | -4632550.9462 | -4622518.8379 | -4438850.1476 | -4456517.9967 | -3978925.0904
Total Net Present Cost | -21436641.101 | -22051960.5442 | -22335839.1281 | -22424429.2969 | -21290100.4538 | -23173480.4883 | -23315163.2112 | -22191557.4367 | -22366051.439 | -21490830.6934 | -17563171.2171 | -17714060.939 | -18002177.999 | -19738148.3767 | -19172172.3545
Marginal Net Present Value (NPC-Baseline) | -21163312303.8905 | -21163927623.3337 | -21164211501.9175 | -21164300092.0864 | -21163165763.2433 | -21165049143.2778 | -21165190826.0007 | -21164067220.2262 | -21164241714.2284 | -21163366493.4829 | -21159438834.0066 | -21159589723.7285 | -21159877840.7885 | -21161613811.1662 | -21161047835.1439
Net Reduction in Imported Fuel | 12.1% | 17.97% | 20.68% | 20.73% | 29.38% | 25.12% | 25.16% | 33.44% | 33.27% | 40.96% | 58.24% | 58.1% | 60.29% | 56.82% | 62.98%
Marginal NPV = NPC - NPC(baseline) - capital investment | Highest NPV Cases
Marginal NPV (Utility Only) | 322318.1437 | -164377.1298 | -452984.8626 | -541591.706 | 720645.1291 | -1506307.498 | -1648045.0086 | -458558.9132 | -637142.2445 | 268383.3429 | 4091239.8088 | 3930330.4386 | 3462674.7782 | 1742434.1297 | 1841574.3456
Marginal NPV (Heating Customers Only) | 1477344.0172 | 1348719.8475 | 1353448.9965 | 1353465.671 | 1225557.679 | 1569130.2716 | 1569185.0593 | 1503304.7384 | 1507394.0674 | 1477089.2256 | 1581892.2361 | 1591911.8843 | 1771450.4847 | 1755720.7555 | 2222556.5619
Total Marginal NPV | 1799662.1609 | 1184342.7177 | 900464.1339 | 811873.965 | 1946202.8081 | 62822.7736 | -78859.9493 | 1044745.8253 | 870251.823 | 1745472.5685 | 5673132.0448 | 5522242.3229 | 5234125.2629 | 3498154.8852 | 4064130.9075
Total % ROI | 447.1% | 175% | 143.3% | 136.9% | 164.2% | 102% | 97.54% | 125.9% | 120.9% | 136.8% | 206% | 200.9% | 189.4% | 156.9% | 159.2%
Normalized to Energy Efficient System
Normalized NPV (Utility Only) |  | -486695.2735 | -775303.0064 | -863909.8497 | 398326.9854 | -1828625.6417 | -1970363.1523 | -780877.0569 | -959460.3882 | -53934.8008 | 3768921.665 | 3608012.2949 | 3140356.6345 | 1420115.986 | 1519256.2019
Normalized NPV (Heating Customers Only) |  | -128624.1697 | -123895.0207 | -123878.3462 | -251786.3382 | 91786.2543 | 91841.042 | 25960.7212 | 30050.0502 | -254.7916 | 104548.2188 | 114567.8671 | 294106.4675 | 278376.7383 | 745212.5446
Normalized Total NPV |  | -615319.4432 | -899198.0271 | -987788.1959 | 146540.6472 | -1736839.3874 | -1878522.1102 | -754916.3357 | -929410.338 | -54189.5925 | 3873469.8839 | 3722580.1619 | 3434463.1019 | 1698492.7242 | 2264468.7465
Normalized % ROI |  | 41.96% | 42.41% | 41.25% | 105.8% | 32.34% | 30.09% | 78.55% | 74.46% | 98.72% | 180.2% | 175.2% | 164.4% | 130.1% | 135.7%
No Generator
100kW Diesel
Note on A225: Author: Already Included in Purchase Cost
Note on A234: Author: If the generator utilization is less than 30% then a new small generator is purchased (This assumes that the O&M costs for the generator set would not change as the O&M cost for the new generator would offset some of the O&M cost for the existing generator)
Note on B334: Author: NPV Values are normalized to the Baseline
Note on C334: Author: NPV Values are normalized to the Baseline
Note on D334: Author: NPV Values are normalized to the Baseline
Note on E334: Author: NPV Values are normalized to the Baseline
Note on F334: Author: NPV Values are normalized to the Baseline
Note on G334: Author: NPV Values are normalized to the Baseline
Note on H334: Author: NPV Values are normalized to the Baseline
Note on I334: Author: NPV Values are normalized to the Baseline
Note on J334: Author: NPV Values are normalized to the Baseline
Note on K334: Author: NPV Values are normalized to the Baseline
Note on L334: Author: NPV Values are normalized to the Baseline
Note on M334: Author: NPV Values are normalized to the Baseline
Note on N334: Author: NPV Values are normalized to the Baseline
Note on O334: Author: NPV Values are normalized to the Baseline
Note on P334: Author: NPV Values are normalized to the Baseline
Note on A335: Author: Value of Heating Fuel Deferred - Cost of Stove System
Note on B335: Author: NPV Values are normalized to the Baseline
Note on A341: Author: Value of Heating Fuel Deferred - Cost of Stove System

## Low-EE no Stoves Detailed
Summary Results
New Solar | No Generator | SG 100 | SG 100 | No Generator | SG 200 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 500 | SG 500 | SG 300
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | WG 100 | No Generator | No Generator | No Generator | WG 100 | WG 200 | WG 200 | WG 500
New Storage | No Battery | No Battery | Bat 100/100 | No Battery | No Battery | No Battery | No Battery | No Battery | Bat 50/50 | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery
New Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel
Energy Efficiency Cost | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169
Renewable Energy Purchase Cost | 0 | -550000 | -670000 | -950000 | -1050000 | -1550000 | -2500000 | -2550000 | -2635000 | -2670000 | -3500000 | -4200000 | -4320000 | -5300000
Stove Purchase Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Generator Purchase Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26
Net Reduction in Imported Fuel | 11.95% | 14.78% | 14.87% | 21.12% | 17.79% | 20.39% | 28.8% | 23.42% | 23.42% | 23.42% | 31.24% | 38.43% | 38.29% | 53.35%
Marginal NPV (Utility Only) | 191270.0033 | -61431.9961 | -68589.5399 | 1724800.036 | -290826.1413 | -367500.0119 | 777853.0146 | -1413984.6108 | -1591131.6414 | -1634486.0925 | -434606.3026 | 401919.3817 | 240816.3508 | 3350161.1791
Marginal NPV (Heating Customers Only) | 1453567.3184 | 1402384.2233 | 1402450.4603 | 1273368.2105 | 1330390.7124 | 1268149.8055 | 1078273.0651 | 1189040.7952 | 1189002.9455 | 1189021.9917 | 1012419.211 | 821572.8149 | 823445.7681 | 414316.5591
Total Marginal NPV | 1644837.3217 | 1340952.2272 | 1333860.9203 | 2998168.2465 | 1039564.5711 | 900649.7936 | 1856126.0797 | -224943.8156 | -402128.6959 | -445464.1008 | 577812.9084 | 1223492.1967 | 1064262.1189 | 3764477.7382
Total % ROI | 417.3% | 225.5% | 212.2% | 304.2% | 166.3% | 143.5% | 161.5% | 92.67% | 87.25% | 86.03% | 114.4% | 125.9% | 122% | 164.7%
Total Capital Cost | 518433.4169 | 1068433.4169 | 1188433.4169 | 1468433.4169 | 1568433.4169 | 2068433.4169 | 3018433.4169 | 3068433.4169 | 3153433.4169 | 3188433.4169 | 4018433.4169 | 4759591.6769 | 4879591.6769 | 5859591.6769
Raw DATA
Simulation Statistics | 1 | 3 | 5 | 6 | 7 | 8 | 9 | 10 | 12 | 13 | 14 | 16 | 18 | 19
Total Sim Time | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Power Utility Statistics
Failure Statistics
Occurrences | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations")
Downtime
Min | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Max | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Average | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Total | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Thermal Load Service
Overall
Overall Energy Availability | 25.1% | 24.3% | 24.3% | 22.28% | 23.18% | 22.2% | 19.24% | 20.97% | 20.97% | 20.97% | 18.21% | 15.22% | 15.25% | 8.859%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Load Served | 13239517 | 12817608 | 12818154 | 11754112 | 12224156 | 11711096 | 10145917 | 11058990 | 11058678 | 11058835 | 9603075 | 8029903 | 8045342 | 4672836
Total Load Not Served | 39507282 | 39929191 | 39928645 | 40992687 | 40522643 | 41035703 | 42600882 | 41687809 | 41688121 | 41687964 | 43143724 | 44716896 | 44701457 | 48073963
Post-Startup
Post-Startup Energy Availability
DBT Occurrences w/ Post-Startup Load Loss
Total Post-Startup Load Served | 13239517 | 12817608 | 12818154 | 11754112 | 12224156 | 11711096 | 10145917 | 11058990 | 11058678 | 11058835 | 9603075 | 8029903 | 8045342 | 4672836
Total Post-Startup Load Not Served | 39507282 | 39929191 | 39928645 | 40992687 | 40522643 | 41035703 | 42600882 | 41687809 | 41688121 | 41687964 | 43143724 | 44716896 | 44701457 | 48073963
Variable Selections
New Solar | No Generator | SG 100 | SG 100 | No Generator | SG 200 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 500 | SG 500 | SG 300
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | WG 100 | No Generator | No Generator | No Generator | WG 100 | WG 200 | WG 200 | WG 500
New Storage | No Battery | No Battery | Bat 100/100 | No Battery | No Battery | No Battery | No Battery | No Battery | Bat 50/50 | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery
Metric Values
Purchase Cost | 0 | 550000 | 670000 | 950000 | 1050000 | 1550000 | 2500000 | 2550000 | 2635000 | 2670000 | 3500000 | 4200000 | 4320000 | 5300000
Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Diesel Fuel Used (Gal/Hour) | 14.11 | 13.46 | 13.44 | 11.99 | 12.75 | 12.14 | 10.17 | 11.42 | 11.42 | 11.42 | 9.59 | 7.88 | 7.91 | 4.32
Heating Fuel Deferred (GHFE/Year) | 13485.1098 | 13055.3744 | 13055.9306 | 11972.1506 | 12450.9139 | 11928.3367 | 10334.1236 | 11264.1341 | 11263.8163 | 11263.9762 | 9781.2119 | 8178.8576 | 8194.583 | 4759.517
Average Renewable Energy Spilled | 0 | 0 | 0 | 581.91 | 52871.43 | 615958.9 | 1147833.68 | 3065274.41 | 3065274.41 | 3065274.41 | 4021216.06 | 5326401.24 | 5308405.09 | 11331293.08
Diesel Utilization | 58.58% | 0.5602 | 0.5618 | 0.5273 | 0.5242 | 0.4961 | 0.4131 | 0.4627 | 0.4638 | 46.43% | 38.64% | 29.25% | 29.53% | 15.61%
Heating Fuel Deferred from Waste Heat (GHFE/Year) | 13485.1098 | 13055.3744 | 13055.9306 | 11972.1506 | 12450.9139 | 11928.3367 | 10334.1236 | 11264.1341 | 11263.8163 | 11263.9762 | 9781.2119 | 8178.8576 | 8194.583 | 4759.517
Heating Fuel Deferred from Stoves (GHFE/Year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost
Fixed Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Cost | 0 | 550000 | 670000 | 950000 | 1050000 | 1550000 | 2500000 | 2550000 | 2635000 | 2670000 | 3500000 | 4200000 | 4320000 | 5300000
Total Cost | 0 | 550000 | 670000 | 950000 | 1050000 | 1550000 | 2500000 | 2550000 | 2635000 | 2670000 | 3500000 | 4200000 | 4320000 | 5300000
Generation
Total Diesel Generation
Total Solar Generation | 0 | 10 | 10 | 10 | 20 | 30 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 30
Total Wind Generation | 0 | 0 | 0 | 0 | 0 | 0% | 10 | 0 | 0 | 0% | 1000% | 2000% | 20 | 50
Overall Diesel Efficiency | 34.95% | 34.41% | 34.42% | 34.1% | 32.75% | 30.89% | 28.44% | 28.73% | 28.83% | 28.83% | 26.44% | 22.88% | 23% | 11.88%
Overall Diesel Utilization | 58.58% | 56.02% | 56.18% | 52.73% | 52.42% | 49.61% | 41.31% | 46.27% | 46.38% | 46.43% | 38.64% | 29.25% | 29.53% | 15.61%
Solar Generated
Min | 0% | 226109330% | 226109330% | 0% | 446931517% | 616732100% | 616732100% | 824019209% | 824019209% | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 6167321
Max | 0% | 226109330% | 226109330% | 0% | 446931517% | 6167321 | 616732100% | 8240192.09 | 824019209% | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 6167321
Average | 0% | 2261093.3 | 2261093.3 | 0 | 4469315.17 | 6167321 | 6167321 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 6167321
Total | 0% | 2261093.3 | 2261093.3 | 0 | 4469315.17 | 6167321 | 6167321 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 8240192.09 | 6167321
Solar Spilled
Min | 0 | 0 | 0 | 0 | 52871.43 | 615958.9 | 615958.9 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 615958.9
Max | 0 | 0 | 0 | 0 | 52871.43 | 615958.9 | 615958.9 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 615958.9
Average | 0 | 0 | 0 | 0 | 52871.43 | 615958.9 | 615958.9 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 615958.9
Total | 0 | 0 | 0 | 0 | 52871.43 | 615958.9 | 615958.9 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 3065274.41 | 615958.9
Wind Generated
Min | 0 | 0 | 0 | 6886679.08 | 0 | 0 | 6390680.3 | 0 | 0 | 0 | 5906459.41 | 11710993.37 | 11606394.48 | 23489192.3
Max | 0 | 0 | 0 | 6886679.08 | 0 | 0 | 6390680.3 | 0 | 0 | 0 | 5906459.41 | 11710993.37 | 11606394.48 | 23489192.3
Average | 0 | 0 | 0 | 6886679.08 | 0 | 0 | 6390680.3 | 0 | 0 | 0 | 5906459.41 | 11710993.37 | 11606394.48 | 23489192.3
Total | 0 | 0 | 0 | 6886679.08 | 0 | 0 | 6390680.3 | 0 | 0 | 0 | 5906459.41 | 11710993.37 | 11606394.48 | 23489192.3
Wind Spilled
Min | 0 | 0 | 0 | 581.91 | 0 | 0 | 531874.79 | 0 | 0 | 0 | 955941.65 | 2261126.83 | 2243130.68 | 10715334.18
Max | 0 | 0 | 0 | 581.91 | 0 | 0 | 531874.79 | 0 | 0 | 0 | 955941.65 | 2261126.83 | 2243130.68 | 10715334.18
Average | 0 | 0 | 0 | 581.91 | 0 | 0 | 531874.79 | 0 | 0 | 0 | 955941.65 | 2261126.83 | 2243130.68 | 10715334.18
Total | 0 | 0 | 0 | 581.91 | 0 | 0 | 531874.79 | 0 | 0 | 0 | 955941.65 | 2261126.83 | 2243130.68 | 10715334.18
Weight
Fixed Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Volume
Fixed Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Average | 189.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4
Max | 379.4 | 379.4 | 379.4 | 379.4 | 379.4 | 379.4 | 379.4 | 379.4 | 379.4 | 379.4 | 379.4 | 379.4 | 379.4 | 379.4
Tier (Only)
Load Service
Priority
Overall
Overall Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Load Served | 4149590200% | 4149588400% | 4149591400% | 4149587700% | 4149588800% | 4149589200% | 4149589100% | 4149591200% | 4149590600% | 41495915 | 41495893 | 41495901 | 41495918 | 41495915
Total Load Not Served | 3200% | 5000% | 2100% | 5700% | 4700% | 4200% | 4400% | 2300% | 2900% | 19 | 41 | 33 | 17 | 19
Post-Startup
Post-Startup Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DBT Occurrences w/ Post-Startup Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Post-Startup Load Served | 4149590255% | 4149588452% | 4149591036% | 4149587472% | 4149588835% | 4149589296% | 4149588819% | 4149591217% | 4149590290% | 41495912.19 | 41495890.41 | 41495898.21 | 41495914.21 | 41495911.85
Total Post-Startup Load Not Served | 3214% | 5017% | 2020% | 5584% | 4634% | 4173% | 4236% | 2252% | 2766% | 18.37 | 40.14 | 32.35 | 16.35 | 18.7
Startup Time
Min | 17% | 0.17 | 1.17 | 1.17 | 0.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Max | 17% | 0.17 | 1.17 | 1.17 | 0.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Average | 0.17 | 0.17 | 1.17 | 1.17 | 0.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Renewable Penetration
Min | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Max | 0% | 87.77% | 87.77% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Average | 0% | 7.53% | 7.53% | 17.65% | 14.81% | 20.1% | 35.84% | 26.22% | 26.22% | 26.22% | 40.41% | 54.09% | 53.8% | 75.32%
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 0.00% | 0% | 50.9% | 50.9% | 7.8% | 50.9% | 50.9% | 3.91% | 50.9% | 50.9% | 50.9% | 4.26% | 3.55% | 3.75% | 4.65%
<= 25.00% | 0% | 37.26% | 37.26% | 65.2% | 27.61% | 22.62% | 44.85% | 17.13% | 17.13% | 17.13% | 41.94% | 18.37% | 18.68% | 11.08%
<= 50.00% | 0% | 10.04% | 10.04% | 26.38% | 9.65% | 8.72% | 26.63% | 7.85% | 7.85% | 7.85% | 23.53% | 27.85% | 27.64% | 7.62%
<= 75.00% | 0% | 1.74% | 1.74% | 0.59% | 6.36% | 5.92% | 8.32% | 4.96% | 4.96% | 4.96% | 7.45% | 19.46% | 19.3% | 10.07%
<= 100.00% | 0% | 0.06% | 0.06% | 0.02% | 5.48% | 11.84% | 16.29% | 19.16% | 19.16% | 19.16% | 22.81% | 30.76% | 30.63% | 66.58%
<= 110.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 120.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 130.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 140.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Diesel Fuel Use
Min | 308947254% | 294697524% | 294432542% | 262568008% | 279327005% | 265971117% | 222697662% | 250051441% | 250202141% | 2501159.42 | 2100439.35 | 1726370.85 | 1733154.08 | 945130.84
Max | 308947254% | 294697524% | 294432542% | 262568008% | 279327005% | 2659711.17 | 222697662% | 2500514.41 | 250202141% | 2501159.42 | 2100439.35 | 1726370.85 | 1733154.08 | 945130.84
Average | 308947254% | 2946975.24 | 2944325.42 | 2625680.08 | 2793270.05 | 2659711.17 | 2226976.62 | 2500514.41 | 2502021.41 | 2501159.42 | 2100439.35 | 1726370.85 | 1733154.08 | 945130.84
Natural Gas Use
Min | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Max | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Average | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Spinning Reserve
Min | 1.04% | 1.04% | 1.04% | 5.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Max | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Average | 40.25% | 43.4% | 43.23% | 47.03% | 47.71% | 50.7% | 59.04% | 54.38% | 54.46% | 54.42% | 61.83% | 71.27% | 71.08% | 84.77%
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 0.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0.01% | 0.01% | 0.02% | 0.01% | 0.01% | 0.03% | 0.02% | 0.06%
<= 5.00% | 0.01% | 0.01% | 0.01% | 0% | 0.01% | 0% | 0% | 0.01% | 0.01% | 0.01% | 0% | 0% | 0% | 0%
<= 10.00% | 0.1% | 0.08% | 0.07% | 0.02% | 0.07% | 0.06% | 0.01% | 0.07% | 0.07% | 0.07% | 0.01% | 0.01% | 0.01% | 0.01%
<= 15.00% | 0.49% | 0.46% | 0.45% | 0.13% | 0.4% | 0.35% | 0.08% | 0.33% | 0.33% | 0.32% | 0.08% | 0.08% | 0.09% | 0.03%
<= 20.00% | 3.44% | 3.45% | 3.46% | 1.2% | 3.02% | 2.78% | 0.75% | 2.54% | 2.45% | 2.42% | 0.72% | 0.47% | 0.5% | 0.29%
<= 25.00% | 6.87% | 6.62% | 6.85% | 2.77% | 5.97% | 5.56% | 1.89% | 5.21% | 5.03% | 5.04% | 1.87% | 1.3% | 1.36% | 0.96%
<= 30.00% | 9.64% | 8.61% | 9.01% | 4.46% | 8.06% | 7.9% | 3.19% | 7.42% | 7.26% | 7.32% | 3.13% | 2.06% | 2.09% | 1.56%
<= 40.00% | 23.84% | 20.17% | 20.45% | 17.74% | 18.71% | 18.98% | 12.24% | 17.85% | 17.94% | 18.28% | 11.77% | 5.31% | 5.39% | 4.03%
<= 50.00% | 35.51% | 28.81% | 27.94% | 32.26% | 25.68% | 23.67% | 21.41% | 22.26% | 22.45% | 22.24% | 20.13% | 8.41% | 8.58% | 4.97%
<= 75.00% | 20.09% | 30.17% | 30.18% | 40.54% | 27.69% | 24.37% | 38.14% | 21.57% | 21.68% | 21.51% | 34.22% | 39.66% | 39.59% | 14.04%
<= 100.00% | 0.02% | 1.61% | 1.59% | 0.87% | 10.38% | 16.33% | 22.28% | 22.74% | 22.76% | 22.77% | 28.05% | 42.65% | 42.36% | 74.05%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Diesel Gen Set Data
JD 6619 Run Time (hours/year) | 3385.4064 | 3769.17 | 3660.6768 | 3398.1732 | 3686.0812 | 3425.4836 | 2694.7168 | 3422.9024 | 3486.2216 | 3466.6864 | 2736.0316 | 2648.5244 | 2691.7848 | 2844.6192
CAT 3406 Run Time (hours/year) | 7548.78 | 7183.61 | 6604.97 | 5016.3932 | 6862.4976 | 5756.5948 | 5027.0836 | 5909.3832 | 6247.0076 | 6221.5248 | 5207.2836 | 4473.2352 | 4531.3172 | 4394.8692
SD 60 Run Time (hours/year) | 702.4476 | 413.2292 | 725.2088 | 1347.89 | 798.052 | 1264.1396 | 1724.4668 | 1032.8768 | 993.0856 | 1067.1548 | 1571.3972 | 2210.5912 | 2126.6344 | 1968.1564
CMS K19G2 Run Time (hours/year) | 17.7372 | 12.7652 | 20.584 | 14.2384 | 33.3188 | 31.2492 | 28.4196 | 31.874 | 19.2988 | 17.6944 | 11.2528 | 234.8296 | 269.3624 | 460.754
Total Run Time | 11654.3712 | 11378.7744 | 11011.4396 | 9776.6948 | 11379.9496 | 10477.4672 | 9474.6868 | 10397.0364 | 10745.6136 | 10773.0604 | 9525.9652 | 9567.1804 | 9619.0988 | 9668.3988
JD 6619 Run Time (hours) | 84635.16 | 94229.25 | 91516.92 | 84954.33 | 92152.03 | 85637.09 | 67367.92 | 85572.56 | 87155.54 | 86667.16 | 68400.79 | 66213.11 | 67294.62 | 71115.48
CAT 3406 Run Time (hours) | 188719.5 | 179590.25 | 165124.25 | 125409.83 | 171562.44 | 143914.87 | 125677.09 | 147734.58 | 156175.19 | 155538.12 | 130182.09 | 111830.88 | 113282.93 | 109871.73
SD 60 Run Time (hours) | 17561.19 | 10330.73 | 18130.22 | 33697.25 | 19951.3 | 31603.49 | 43111.67 | 25821.92 | 24827.14 | 26678.87 | 39284.93 | 55264.78 | 53165.86 | 49203.91
CMS K19G2 Run Time (hours) | 443.43 | 319.13 | 514.6 | 355.96 | 832.97 | 781.23 | 710.49 | 796.85 | 482.47 | 442.36 | 281.32 | 5870.74 | 6734.06 | 11518.85
Total Run Time | 291359.28 | 284469.36 | 275285.99 | 244417.37 | 284498.74 | 261936.68 | 236867.17 | 259925.91 | 268640.34 | 269326.51 | 238149.13 | 239179.51 | 240477.47 | 241709.97
Assumptions
Horizon (years) | 25
Nominal Discount Rate | 3%
Load Inflation Rate | 1%
Fuel Cost Adjustment | 1
Heating fuel cost ($/gal) | 7.99
Diesel oil cost ($/gal) | 7.1633
HHV (Btu/gallon) | 134000
Conversion (kWh/Btu) | 0.00029307
Baseline total fuel use (gal/year) | 186075.5898
Baseline Gen O&M net present cost | -2655676.211
Baseline diesel fuel net present cost | -13815874.8773
Baseline heating fuel net present cost | -6752037.5899
Baseline total net present cost | 21141875662.7895
Energy Efficiency Cost Electrical Curve | 0.1493
Energy Efficiency Cost Electrical Curve | -0.9009
Energy Efficiency Cost Electrical Curve | 16.515
Energy Efficiency Cost Thermal Curve | 0.1123
Energy Efficiency Cost Thermal Curve | -0.6774
Energy Efficiency Cost Thermal Curve | 12.418
Baseline electrical load (kWh/year) | 1747196.0752
Baseline thermal load (kWh/year) | 2813162.6652
EE electrical load(kWh/year) | 1659836.08
EE thermal load(kWh/year) | 2109871.96
Assumed replacement usage (hours) | 80000
Gen replacement curve ($/kW) | 410.53
Gen replacement curve ($) | 105.26
202kW Gen O&M | 15.7808
314kW Gen O&M | 16.4528
365kW Gen O&M | 16.7588
397kW Gen O&M | 17.1422
Wind Replacement cost (First turbine) | 560000
Wind O&M Cost ($/kWh) | 17500
Solar O&M Cost ($/hour/100kW) | 0.54
EE electrical load reduction (%) | 0.05
EE thermal load reduction (%) | 0.25
EE electrical load reduction cost ($/kWh/year) | 0.14554
EE thermal load reduction cost ($/kWh/year) | 0.71908
EE electrical load reduction cost ($/kWh/year) | -12714.5993
EE thermal load reduction cost ($/kWh/year) | -505718.8176 | -518433.4169
Financial calculations
RE Purchase Cost | 0 | -550000 | -670000 | -950000 | -1050000 | -1550000 | -2500000 | -2550000 | -2635000 | -2670000 | -3500000 | -4200000 | -4320000 | -5300000
Stove Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kW of Stoves | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
# of Stoves | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gen Replacement Cost (per year)
JD 6619 | -3513.7268 | -3912.0366 | -3799.4311 | -3526.9776 | -3825.7984 | -3555.3231 | -2796.8573 | -3552.6441 | -3618.3633 | -3598.0877 | -2839.7381 | -2748.9141 | -2793.8142 | -2952.4416
CAT 3406 | -12173.5099 | -11584.6199 | -10651.4785 | -8089.6664 | -11066.7793 | -9283.3496 | -8106.9063 | -9529.7432 | -10074.2118 | -10033.1171 | -8397.5051 | -7213.7449 | -7307.4106 | -7087.3682
SD 60 | -1316.6389 | -774.5398 | -1359.3016 | -2526.4296 | -1495.8358 | -2369.4513 | -3232.2697 | -1935.9818 | -1861.3988 | -2000.2311 | -2945.3623 | -4143.4412 | -3986.0761 | -3689.0314
CMS | -36.1585 | -26.0228 | -41.9619 | -29.026 | -67.9227 | -63.7037 | -57.9354 | -64.9774 | -39.342 | -36.0713 | -22.9396 | -478.7168 | -549.1143 | -939.2797
New Small (100kW) Gen (purchase) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26
Gen O&M Cost (per year)
JD 6619 | -53424.252 | -59480.3295 | -57768.2254 | -53625.7217 | -58169.1259 | -54056.7003 | -42524.6521 | -54015.967 | -55015.1915 | -54706.9114 | -43176.6307 | -41795.7014 | -42478.383 | -44890.2244
CAT 3406 | -124198.1901 | -118190.1394 | -108669.9202 | -82533.4632 | -112906.9574 | -94711.8151 | -82709.3497 | -97225.6044 | -102780.4543 | -102361.1922 | -85674.1352 | -73597.0204 | -74552.6291 | -72307.6842
SD 60 | -11772.1437 | -6925.2049 | -12153.593 | -22588.9515 | -13374.354 | -21185.3995 | -28899.908 | -17309.7241 | -16642.8733 | -17884.1805 | -26334.6528 | -37046.7453 | -35639.7343 | -32983.8411
CMS | -304.0554 | -218.8242 | -352.856 | -244.0781 | -571.159 | -535.6814 | -487.1757 | -546.3919 | -330.8247 | -303.3217 | -192.8982 | -4025.5064 | -4617.4761 | -7898.3578
Deasil Fuel use (Gal/year) | 123603.6 | 117909.6 | 117734.4 | 105032.4 | 111690 | 106346.4 | 89089.2 | 100039.2 | 100039.2 | 100039.2 | 84008.4 | 69028.8 | 69291.6 | 37843.2
Heating Fuel use (Gal/year) | 40240.1415 | 40669.8769 | 40669.3208 | 41753.1007 | 41274.3374 | 41796.9147 | 43391.1277 | 42461.1172 | 42461.435 | 42461.2751 | 43944.0394 | 45546.3938 | 45530.6684 | 48965.7343
Total Fuel usage (Gal/year) | 163843.7415 | 158579.4769 | 158403.7208 | 146785.5007 | 152964.3374 | 148143.3147 | 132480.3277 | 142500.3172 | 142500.635 | 142500.4751 | 127952.4394 | 114575.1938 | 114822.2684 | 86808.9343
New Wind Turbines (#) | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2 | 2 | 5
New 100kW Solar Fields (#) | 0 | 1 | 1 | 0 | 2 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 3
Wind Replacement Cost (per replacement) | 0 | 0 | 0 | -560000 | 0 | 0 | -560000 | 0 | 0 | 0 | -560000 | -1092000 | -1092000 | -2520000
Wind Replacement NPV (Turbines are replaced every 20 years: this means that the first replacement is out of the time horizon for this analysis and so the replacement cost is not used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Replacement NPV (converter only after 10 years) | 0 | -63211.8617 | -63211.8617 | 0 | -126423.7234 | -189635.5851 | -189635.5851 | -316059.3085 | -316059.3085 | -316059.3085 | -316059.3085 | -316059.3085 | -316059.3085 | -189635.5851
Wind O&M Cost per year ($/year) | 0 | -17500 | -17500 | 0 | -34562.5 | -51187.5 | -51187.5 | -83125 | -83125 | -83125 | -83125 | -83125 | -83125 | -51187.5
Solar O&M Cost per year ($/year) | 0 | -4730.4 | -4730.4 | 0 | -9460.8 | -14191.2 | -14191.2 | -23652 | -23652 | -23652 | -23652 | -23652 | -23652 | -14191.2
Gen + Wind + Solar O&M + Genorator Replacement Cost
Year
1 | -206738.6755 | -223342.1171 | -217027.1676 | -173164.3142 | -245501.2326 | -251140.1241 | -234193.7542 | -290958.0339 | -297139.6598 | -297700.1129 | -276360.8621 | -277826.7905 | -278701.6376 | -238126.9285
2 | -194871.0298 | -210521.3659 | -204568.9203 | -163223.9742 | -231408.4575 | -236723.6536 | -220750.0746 | -274255.8525 | -280082.6278 | -280610.9086 | -260496.6181 | -261878.3962 | -262703.0235 | -224457.4686
3 | -189195.1745 | -204389.6756 | -198610.6022 | -158469.8778 | -224668.4053 | -229828.7899 | -214320.4608 | -266267.818 | -271924.8813 | -272437.7753 | -252909.3379 | -254250.8701 | -255051.4791 | -217919.8725
4 | -183684.6355 | -198436.5783 | -192825.8274 | -153854.2503 | -218124.6654 | -223134.7474 | -208078.1173 | -258512.4446 | -264004.7391 | -264502.6945 | -245543.0465 | -246845.5049 | -247622.7952 | -211572.6917
5 | -178334.5975 | -192656.8721 | -187209.5412 | -149373.0586 | -211771.5198 | -216635.6771 | -202017.5896 | -250982.956 | -256315.2807 | -256798.7325 | -238391.3073 | -239655.83 | -240410.4808 | -205410.3803
6 | -173140.386 | -187045.5069 | -181756.8361 | -145022.3869 | -205603.4173 | -210325.9001 | -196133.5821 | -243672.7728 | -248849.7871 | -249319.1578 | -231447.8712 | -232675.5631 | -233408.2338 | -199427.5537
7 | -168097.4621 | -181597.5795 | -176462.9477 | -140798.4339 | -199614.9682 | -204199.903 | -190420.9535 | -236575.5076 | -241601.7351 | -242057.4347 | -224706.6711 | -225898.605 | -226609.9357 | -193618.9842
8 | -163201.4195 | -176308.3296 | -171323.2502 | -136697.5087 | -193800.94 | -198252.333 | -184874.7122 | -229684.9588 | -234564.7913 | -235007.2182 | -218161.8166 | -219319.034 | -220009.6463 | -187979.5963
9 | -158447.9801 | -171173.1356 | -166333.2526 | -132716.0278 | -188156.2525 | -192477.9932 | -179490.0118 | -222995.1056 | -227732.8071 | -228162.3478 | -211807.5889 | -212931.1009 | -213601.5984 | -182504.4624
10 | -153832.9904 | -166187.5103 | -161488.5947 | -128850.5125 | -182675.9733 | -186871.8381 | -174262.1474 | -216500.1025 | -221099.8127 | -221516.8425 | -205638.4358 | -206729.2242 | -207380.1926 | -177188.7985
11 | -149352.4179 | -161347.0973 | -156785.0434 | -125097.5849 | -177355.3138 | -181428.969 | -169186.5509 | -210194.2743 | -214660.0124 | -215064.8956 | -199648.9668 | -200707.9847 | -201339.9928 | -172027.9597
12 | -145002.3474 | -156647.6673 | -152218.4888 | -121453.9659 | -172189.6251 | -176144.6301 | -164258.7873 | -204072.111 | -208407.779 | -208800.8695 | -193833.9484 | -194862.121 | -195475.7212 | -167017.4366
13 | -140778.9781 | -152085.1139 | -147784.9406 | -117916.4718 | -167174.3933 | -171014.204 | -159474.5507 | -198128.2631 | -202337.6495 | -202719.2908 | -188188.2994 | -189186.5253 | -189782.2536 | -162152.851
14 | -136678.6195 | -147655.4504 | -143480.5248 | -114482.0114 | -162305.2362 | -166033.2078 | -154829.6609 | -192357.537 | -196444.3199 | -196814.8454 | -182707.0868 | -183676.2381 | -184254.6151 | -157429.9525
15 | -132697.6888 | -143354.8062 | -139301.4804 | -111147.5839 | -157577.8992 | -161197.2891 | -150320.0591 | -186754.8903 | -190722.6407 | -191082.3742 | -177385.5211 | -178326.4448 | -178887.9759 | -152844.614
16 | -128832.7076 | -139179.4235 | -135244.1557 | -107910.2756 | -152988.2517 | -156502.2224 | -145941.805 | -181315.4275 | -185167.6123 | -185516.8682 | -172218.9526 | -173132.4707 | -173677.6465 | -148392.8292
17 | -125080.2987 | -135125.6539 | -131305.0056 | -104767.2579 | -148532.2832 | -151943.9053 | -141691.0728 | -176034.3956 | -179774.3809 | -180113.4642 | -167202.8666 | -168089.7774 | -168619.0742 | -144070.7079
18 | -121437.1832 | -131189.9552 | -127480.5879 | -101715.7844 | -144206.1002 | -147518.3546 | -137564.1483 | -170907.1802 | -174538.2339 | -174867.441 | -162332.8802 | -163193.9586 | -163707.8391 | -139874.4737
19 | -117900.1778 | -127368.8886 | -123767.5611 | -98753.1887 | -140005.9225 | -143221.7035 | -133557.4256 | -165929.3011 | -169454.596 | -169774.2146 | -157604.738 | -158440.7365 | -158939.6496 | -135800.4599
20 | -114466.1921 | -123659.1151 | -120162.6807 | -95876.8822 | -135928.0801 | -139050.1976 | -129667.4035 | -161096.4089 | -164519.0252 | -164829.3345 | -153014.3088 | -153825.9578 | -154310.3394 | -131845.1067
Total Gen O&M + Replacement Cost | -3081770.9619 | -3329271.8423 | -3235137.409 | -2581291.3517 | -3659588.9371 | -3743645.6431 | -3491032.8677 | -4337195.3413 | -4429342.3718 | -4437696.823 | -4119601.1242 | -4182611.3938 | -4195652.3905 | -3590821.3878
Diesel Fuel Cost
Year
1 | -885413.788 | -844625.768 | -843370.752 | -752382.092 | -800072.7 | -761794.712 | -638175.636 | -716614.136 | -716614.136 | -716614.136 | -601780.172 | -494476.304 | -496358.828 | -271083.456
2 | -834587.4145 | -796140.7937 | -794957.8207 | -709192.282 | -754145.254 | -718064.5791 | -601541.7438 | -675477.553 | -675477.553 | -675477.553 | -567235.5283 | -466091.3413 | -467865.8007 | -255522.1567
3 | -810279.0432 | -772952.2269 | -771803.7094 | -688536.1961 | -732179.8583 | -697150.0768 | -584021.1105 | -655803.4495 | -655803.4495 | -655803.4495 | -550714.1052 | -452515.8654 | -454238.6415 | -248079.7637
4 | -786678.6827 | -750439.0552 | -749323.9897 | -668481.7438 | -710854.2313 | -676844.7348 | -567010.7869 | -636702.3782 | -636702.3782 | -636702.3782 | -534673.8885 | -439335.7916 | -441008.3898 | -240854.1396
5 | -763765.7113 | -728581.607 | -727499.0192 | -649011.4018 | -690149.7392 | -657130.8105 | -550495.9096 | -618157.6487 | -618157.6487 | -618157.6487 | -519100.8626 | -426539.6035 | -428163.4852 | -233838.9704
6 | -741520.1081 | -707360.7835 | -706309.7273 | -630108.1571 | -670048.2905 | -637991.0781 | -534462.0481 | -600153.057 | -600153.057 | -600153.057 | -503981.42 | -414116.1199 | -415692.7041 | -227028.1266
7 | -719922.435 | -686758.0422 | -685737.5994 | -611755.4923 | -650532.3208 | -619408.8137 | -518895.1924 | -582672.8709 | -582672.8709 | -582672.8709 | -489302.3495 | -402054.4853 | -403585.1496 | -220415.6569
8 | -698953.8204 | -666755.3808 | -665764.6596 | -593937.3712 | -631584.7775 | -601367.7803 | -503781.7402 | -565701.8164 | -565701.8164 | -565701.8164 | -475050.8248 | -390344.1605 | -391830.2424 | -213995.7834
9 | -678595.9422 | -647335.3212 | -646373.4559 | -576638.2244 | -613189.1044 | -583852.2139 | -489108.4856 | -549225.0645 | -549225.0645 | -549225.0645 | -461214.393 | -378974.9131 | -380417.711 | -207762.8965
10 | -658831.0118 | -628480.8943 | -627547.0446 | -559842.9363 | -595329.2275 | -566846.8096 | -474862.6074 | -533228.2179 | -533228.2179 | -533228.2179 | -447780.9641 | -367936.8089 | -369337.5835 | -201711.55
11 | -639641.759 | -610175.6256 | -609268.9753 | -543536.8314 | -577989.5413 | -550336.7083 | -461031.6577 | -517697.299 | -517697.299 | -517697.299 | -434738.8001 | -357220.2028 | -358580.1782 | -195836.4563
12 | -621011.4165 | -592403.52 | -591523.277 | -527705.6615 | -561154.8945 | -534307.4838 | -447603.5511 | -502618.7369 | -502618.7369 | -502618.7369 | -422076.5049 | -346815.7309 | -348136.0953 | -190132.4819
13 | -602923.7054 | -575149.0485 | -574294.4437 | -512335.5937 | -544810.5772 | -518745.1299 | -434566.5545 | -487979.3562 | -487979.3562 | -487979.3562 | -409783.0145 | -336714.3018 | -337996.209 | -184594.6426
14 | -585362.8208 | -558397.1345 | -557567.4211 | -497413.1978 | -528942.3079 | -503636.0485 | -421909.2762 | -473766.3652 | -473766.3652 | -473766.3652 | -397847.5869 | -326907.0891 | -328151.6593 | -179218.0996
15 | -568313.4182 | -542133.1403 | -541327.5933 | -482925.4348 | -513536.2213 | -488967.0374 | -409620.6565 | -459967.3449 | -459967.3449 | -459967.3449 | -386259.7931 | -317385.5234 | -318593.8439 | -173998.155
16 | -551760.6002 | -526342.8546 | -525560.7702 | -468859.6454 | -498578.8556 | -474725.279 | -397689.9578 | -446570.2377 | -446570.2377 | -446570.2377 | -375009.5079 | -308141.2849 | -309314.4116 | -168930.2475
17 | -535689.9031 | -511012.4802 | -510253.1749 | -455203.5392 | -484057.1414 | -460898.3291 | -386106.7551 | -433563.3376 | -433563.3376 | -433563.3376 | -364086.9008 | -299166.296 | -300305.254 | -164009.9491
18 | -520087.2846 | -496128.6216 | -495391.4319 | -441945.1837 | -469958.3897 | -447474.1059 | -374860.9273 | -420935.2792 | -420935.2792 | -420935.2792 | -353482.428 | -290452.7146 | -291558.499 | -159232.9603
19 | -504939.1112 | -481678.2734 | -480962.5553 | -429072.9939 | -456270.2812 | -434440.8796 | -363942.6479 | -408675.0284 | -408675.0284 | -408675.0284 | -343186.8233 | -281992.9268 | -283066.5039 | -154595.1071
20 | -490232.1468 | -467648.8091 | -466953.9372 | -416575.7222 | -442980.8556 | -421787.2617 | -353342.3766 | -396771.8722 | -396771.8722 | -396771.8722 | -333191.0906 | -273779.5405 | -274821.8484 | -150092.3369
Total Diesel Fuel Cost | -13198510.1232 | -12590499.3804 | -12571791.3576 | -11215459.7007 | -11926364.5691 | -11355769.8721 | -9513029.621 | -10682281.0494 | -10682281.0494 | -10682281.0494 | -8970496.9583 | -7370961.0043 | -7399023.0386 | -4040932.9364
Heating Fuel Cost
Year
1 | -321518.7305 | -324952.3164 | -324947.873 | -333607.2749 | -329781.956 | -333957.3483 | -346695.1105 | -339264.3267 | -339266.8658 | -339265.5881 | -351112.8751 | -363915.6861 | -363790.0402 | -391236.217
2 | -303062.2401 | -306298.7241 | -306294.5357 | -314456.8525 | -310851.1227 | -314786.8303 | -326793.3929 | -319789.1665 | -319791.5598 | -319790.3555 | -330957.5597 | -343025.437 | -342907.0037 | -368777.6577
3 | -294235.1846 | -297377.4021 | -297373.3357 | -305297.9151 | -301797.2065 | -305618.2819 | -317275.1387 | -310474.9189 | -310477.2426 | -310476.0733 | -321318.0191 | -333034.4048 | -332919.4211 | -358036.5609
4 | -285665.2277 | -288715.9243 | -288711.9764 | -296405.7428 | -293006.9966 | -296716.7785 | -308034.1153 | -301431.9601 | -301434.2161 | -301433.0809 | -311959.2419 | -323334.3736 | -323222.7389 | -347608.3115
5 | -277344.8813 | -280306.7226 | -280302.8897 | -287772.5658 | -284472.8122 | -288074.5422 | -299062.2479 | -292652.3885 | -292654.5787 | -292653.4766 | -302873.0504 | -313916.8676 | -313808.4844 | -337483.7976
6 | -269266.875 | -272142.4492 | -272138.7278 | -279390.8406 | -276187.1963 | -279684.0216 | -290351.6969 | -284128.5325 | -284130.659 | -284129.5889 | -294051.5052 | -304773.6579 | -304668.4314 | -327654.1724
7 | -261424.1505 | -264215.9701 | -264212.3571 | -271253.2433 | -268142.909 | -271537.885 | -281894.8514 | -275852.9442 | -275855.0087 | -275853.9698 | -285486.8983 | -295896.7552 | -295794.5936 | -318110.847
8 | -253809.8549 | -256520.3593 | -256516.8516 | -263352.6634 | -260332.9214 | -263629.0146 | -273684.3217 | -267818.3924 | -267820.3968 | -267819.3882 | -277171.7459 | -287278.4031 | -287179.2171 | -308845.4825
9 | -246417.3348 | -249048.8925 | -249045.487 | -255682.1975 | -252750.4091 | -255950.4996 | -265712.9337 | -260017.8567 | -260019.8027 | -260018.8235 | -269098.7824 | -278911.071 | -278814.7739 | -299849.983
10 | -239240.1309 | -241795.0413 | -241791.7349 | -248235.1432 | -245388.7467 | -248495.6307 | -257973.7221 | -252444.5211 | -252446.4104 | -252445.4597 | -261260.9538 | -270787.4476 | -270693.9552 | -291116.4884
11 | -232271.9718 | -234752.4673 | -234749.2572 | -241004.9934 | -238241.5017 | -241257.8939 | -250459.9243 | -245091.768 | -245093.6023 | -245092.6793 | -253651.4115 | -262900.4345 | -262809.6653 | -282637.3674
12 | -225506.7687 | -227915.0168 | -227911.9002 | -233985.4305 | -231302.4288 | -234230.9649 | -243164.9751 | -237953.1728 | -237954.9537 | -237954.0576 | -246263.5063 | -255243.1403 | -255155.0148 | -274405.211
13 | -218938.6104 | -221276.7153 | -221273.6895 | -227170.3208 | -224565.4649 | -227408.7038 | -236082.5001 | -231022.4979 | -231024.2269 | -231023.3569 | -239090.7828 | -247808.8741 | -247723.3154 | -266412.8262
14 | -212561.7577 | -214831.7624 | -214828.8248 | -220553.7096 | -218024.7232 | -220785.1493 | -229206.3108 | -224293.6873 | -224295.3659 | -224294.5212 | -232126.9736 | -240591.1399 | -240508.0732 | -258653.2294
15 | -206370.6385 | -208574.5266 | -208571.6745 | -214129.8151 | -211674.4885 | -214354.5139 | -222530.3988 | -217760.8614 | -217762.4912 | -217761.6711 | -225365.9938 | -233583.631 | -233502.9837 | -251119.6402
16 | -200359.8432 | -202499.5404 | -202496.7714 | -207893.0244 | -205509.2121 | -208111.1786 | -216048.9309 | -211418.3121 | -211419.8944 | -211419.0981 | -218801.9357 | -226780.2242 | -226701.9259 | -243805.4759
17 | -194524.1196 | -196601.4955 | -196598.8072 | -201837.8877 | -199523.5069 | -202049.6879 | -209756.2436 | -205260.4972 | -205262.0334 | -205261.2603 | -212429.0638 | -220174.975 | -220098.9572 | -236704.3455
18 | -188858.3686 | -190875.2384 | -190872.6283 | -195959.1143 | -193712.1427 | -196164.7456 | -203646.8384 | -199282.0361 | -199283.5275 | -199282.777 | -206241.8095 | -213762.1116 | -213688.3079 | -229810.0442
19 | -183357.6394 | -185315.7654 | -185313.2314 | -190251.5673 | -188070.0414 | -190451.2093 | -197715.3771 | -193477.7049 | -193479.1529 | -193478.4243 | -200234.7665 | -207536.0307 | -207464.3766 | -223116.5478
20 | -178017.1256 | -179918.2189 | -179915.7586 | -184710.2595 | -182592.2732 | -184904.0867 | -191956.6768 | -187842.432 | -187843.8378 | -187843.1304 | -194402.6859 | -201491.292 | -201421.7249 | -216618.0075
Total Heating Fuel Cost | -4792751.4538 | -4843934.549 | -4843868.312 | -4972950.5618 | -4915928.0598 | -4978168.9667 | -5168045.7071 | -5057277.977 | -5057315.8267 | -5057296.7806 | -5233899.5612 | -5424745.9573 | -5422873.0041 | -5832002.2131
Total Net Present Cost | -21591465.9558 | -21895351.0503 | -21902442.3572 | -20238135.0311 | -22196738.7064 | -22335653.4839 | -21380177.1978 | -23461247.0932 | -23638431.9734 | -23681767.3784 | -22658490.3691 | -22012811.0808 | -22172041.1586 | -19471825.5393
Marginal Net Present Value (NPC-Baseline) | -21163467128.7453 | -21163771013.8398 | -21163778105.1467 | -21162113797.8205 | -21164072401.4959 | -21164211316.2734 | -21163255839.9873 | -21165336909.8826 | -21165514094.7629 | -21165557430.1679 | -21164534153.1586 | -21163888473.8703 | -21164047703.9481 | -21161347488.3288
Net Reduction in Imported Fuel | 11.95% | 14.78% | 14.87% | 21.12% | 17.79% | 20.39% | 28.8% | 23.42% | 23.42% | 23.42% | 31.24% | 38.43% | 38.29% | 53.35%
Marginal NPV = NPC - NPC(baseline) - capital investment | Highest NPV Cases
Marginal NPV (Utility Only) | 191270.0033 | -61431.9961 | -68589.5399 | 1724800.036 | -290826.1413 | -367500.0119 | 777853.0146 | -1413984.6108 | -1591131.6414 | -1634486.0925 | -434606.3026 | 401919.3817 | 240816.3508 | 3350161.1791
Marginal NPV (Heating Customers Only) | 1453567.3184 | 1402384.2233 | 1402450.4603 | 1273368.2105 | 1330390.7124 | 1268149.8055 | 1078273.0651 | 1189040.7952 | 1189002.9455 | 1189021.9917 | 1012419.211 | 821572.8149 | 823445.7681 | 414316.5591
Total Marginal NPV | 1644837.3217 | 1340952.2272 | 1333860.9203 | 2998168.2465 | 1039564.5711 | 900649.7936 | 1856126.0797 | -224943.8156 | -402128.6959 | -445464.1008 | 577812.9084 | 1223492.1967 | 1064262.1189 | 3764477.7382
Total % ROI | 417.3% | 225.5% | 212.2% | 304.2% | 166.3% | 143.5% | 161.5% | 92.67% | 87.25% | 86.03% | 114.4% | 125.9% | 122% | 164.7%
Normalized to Energy Efficient System
Normalized NPV (Utility Only) |  | -252701.9993 | -259859.5432 | 1533530.0327 | -482096.1445 | -558770.0152 | 586583.0113 | -1605254.6141 | -1782401.6446 | -1825756.0958 | -625876.3059 | 210649.3785 | 49546.3475 | 3158891.1759
Normalized NPV (Heating Customers Only) |  | -51183.0951 | -51116.8582 | -180199.1079 | -123176.606 | -185417.5129 | -375294.2533 | -264526.5232 | -264564.3729 | -264545.3268 | -441148.1074 | -631994.5035 | -630121.5503 | -1039250.7593
Normalized Total NPV |  | -303885.0945 | -310976.4013 | 1353330.9248 | -605272.7505 | -744187.5281 | 211288.758 | -1869781.1373 | -2046966.0175 | -2090301.4225 | -1067024.4133 | -421345.125 | -580575.2028 | 2119640.4165
Normalized % ROI |  | 44.75% | 53.59% | 242.5% | 42.35% | 51.99% | 108.5% | 26.68% | 22.32% | 21.71% | 69.51% | 89.97% | 86.56% | 140%
No Generator
100kW Diesel
Note on A225: Author: Already Included in Purchase Cost
Note on A234: Author: If the generator utilization is less than 30% then a new small generator is purchased (This assumes that the O&M costs for the generator set would not change as the O&M cost for the new generator would offset some of the O&M cost for the existing generator)
Note on B334: Author: NPV Values are normalized to the Baseline
Note on C334: Author: NPV Values are normalized to the Baseline
Note on D334: Author: NPV Values are normalized to the Baseline
Note on E334: Author: NPV Values are normalized to the Baseline
Note on F334: Author: NPV Values are normalized to the Baseline
Note on G334: Author: NPV Values are normalized to the Baseline
Note on H334: Author: NPV Values are normalized to the Baseline
Note on I334: Author: NPV Values are normalized to the Baseline
Note on J334: Author: NPV Values are normalized to the Baseline
Note on K334: Author: NPV Values are normalized to the Baseline
Note on L334: Author: NPV Values are normalized to the Baseline
Note on M334: Author: NPV Values are normalized to the Baseline
Note on N334: Author: NPV Values are normalized to the Baseline
Note on O334: Author: NPV Values are normalized to the Baseline
Note on A335: Author: Value of Heating Fuel Deferred - Cost of Stove System
Note on B335: Author: NPV Values are normalized to the Baseline
Note on A341: Author: Value of Heating Fuel Deferred - Cost of Stove System

## Med-EE Detailed
Summary Results
New Solar | No Generator | No Generator | SG 200 | SG 200 | SG 300 | SG 300 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 200 | SG 300 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | WG 100 | WG 200 | WG 500 | WG 500 | WG 500
New Storage | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery | Bat 50/50 | Bat 100/100 | No Battery | No Battery | No Battery | No Battery | No Battery | No Battery | No Battery
New Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel
Energy Efficiency Cost | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243
Renewable Energy Purchase Cost | 0 | -85000 | -1050000 | -1135000 | -1550000 | -1635000 | -1670000 | -2500000 | -2550000 | -3500000 | -4200000 | -4800000 | -5300000 | -6300000
Stove Purchase Cost | 0 | 0 | -10181.3 | -10181.3 | -11654.88 | -11654.88 | -11654.88 | -12987.2 | -17540.34 | -19856.83 | -22930.72 | -34482.88 | -38324.11 | -47876.44
New Generator Purchase Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Net Reduction in Imported Fuel | 18.95% | 19% | 24.81% | 24.85% | 27.58% | 27.58% | 27.58% | 36.16% | 31.93% | 40.22% | 47.85% | 64.71% | 66.08% | 69.5%
Marginal NPV (Utility Only) | 1176325.8184 | 1036898.326 | 734855.0889 | 669603.5524 | 359649.3316 | 272931.1603 | 236561.791 | 1445320.9171 | -818448.1176 | 259195.828 | 1020673.6912 | 4636685.8586 | 3865099.5966 | 2355182.0562
Marginal NPV (Heating Customers Only) | 1353967.5006 | 1354004.4227 | 1232731.4889 | 1232741.016 | 1251668.7173 | 1251646.0876 | 1251666.3352 | 1137035.389 | 1489157.4628 | 1435233.3211 | 1413828.1729 | 1642135.4682 | 1828566.0401 | 2304703.2888
Total Marginal NPV | 2530293.3189 | 2390902.7487 | 1967586.5778 | 1902344.5684 | 1611318.0489 | 1524577.2478 | 1488228.1262 | 2582356.3062 | 670709.3452 | 1694429.1492 | 2434501.8641 | 6278821.3268 | 5693665.6366 | 4659885.345
Total % ROI | 278.9% | 259.5% | 179.5% | 174.3% | 154.1% | 149.8% | 148.1% | 165.8% | 116.8% | 134.3% | 143.2% | 200.5% | 184.3% | 160%
Total Capital Cost | 1414120.243 | 1499120.243 | 2474301.543 | 2559301.543 | 2975775.123 | 3060775.123 | 3095775.123 | 3927107.443 | 3981660.583 | 4933977.073 | 5678209.223 | 6289761.383 | 6793602.613 | 7803154.943
Raw DATA
Simulation Statistics | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 12 | 14 | 15 | 17
Total Sim Time | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Power Utility Statistics
Failure Statistics
Occurrences | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations")
Downtime
Min | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Max | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Average | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Total | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Thermal Load Service
Overall
Overall Energy Availability | 27.06% | 27.06% | 24.91% | 24.91% | 23.86% | 23.86% | 23.86% | 20.57% | 22.54% | 19.41% | 16.14% | 9.331% | 9.031% | 8.509%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Load Served | 12367905 | 12368205 | 11386375 | 11386457 | 10906748 | 10906565 | 10906728 | 9402823 | 10305890 | 8872049 | 7376776 | 4265349 | 4128504 | 3889929
Total Load Not Served | 3334598700% | 3334568700% | 34327518 | 34327435 | 34807145 | 34807327 | 34807164 | 36311069 | 35408002 | 36841843 | 38337117 | 41448543 | 41585388 | 41823964
Post-Startup
Post-Startup Energy Availability
DBT Occurrences w/ Post-Startup Load Loss
Total Post-Startup Load Served | 12367905.57 | 12368205.97 | 11386375.17 | 11386457.41 | 10906748.17 | 10906565.67 | 10906728.68 | 9402823.67 | 10305890.75 | 8872049.69 | 7376776.03 | 4265349.95 | 4128504.4 | 3889929.08
Total Post-Startup Load Not Served | 33345987.74 | 33345687.34 | 34327518.14 | 34327435.91 | 34807145.14 | 34807327.64 | 34807164.63 | 36311069.64 | 35408002.56 | 36841843.62 | 38337117.29 | 41448543.36 | 41585388.91 | 41823964.23
Variable Selections
New Solar | No Generator | No Generator | SG 200 | SG 200 | SG 300 | SG 300 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 200 | SG 300 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | WG 100 | WG 200 | WG 500 | WG 500 | WG 500
New Storage | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery | Bat 50/50 | Bat 100/100 | No Battery | No Battery | No Battery | No Battery | No Battery | No Battery | No Battery
Metric Values
Purchase Cost | 0 | 85000 | 1060181.3 | 1145181.3 | 1561654.88 | 1646654.88 | 1681654.88 | 2512987.2 | 2567540.34 | 3519856.83 | 4222930.72 | 4834482.88 | 5338324.11 | 6347876.44
Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Diesel Fuel Used (Gal/Hour) | 13.36 | 13.35 | 12.01 | 12 | 11.44 | 11.44 | 11.44 | 9.51 | 10.75 | 8.94 | 7.3 | 3.95 | 3.84 | 3.58
Heating Fuel Deferred (GHFE/Year) | 12783.35 | 12783.66 | 11850.93 | 11851.01 | 12022.3 | 12022.11 | 12022.28 | 11071.02 | 14065.68 | 13632.38 | 13478.47 | 15492.34 | 17089.87 | 21167.74
Average Renewable Energy Spilled | 0 | 0 | 79408.48 | 79408.48 | 724836.55 | 724836.55 | 724836.55 | 1308393.46 | 3302668.13 | 4317291.16 | 5663656.36 | 10723500.71 | 12405958.22 | 16589881.89
Diesel Utilization | 58.79% | 58.81% | 51.92% | 51.95% | 49.02% | 49.1% | 49.1% | 40.49% | 45.99% | 37.72% | 28.3% | 15.03% | 14.58% | 13.47%
Heating Fuel Deferred from Waste Heat (GHFE/Year) | 12597.3295 | 12597.635 | 11597.5921 | 11597.6756 | 11109.068 | 11108.8816 | 11109.0476 | 9577.2452 | 10497.0641 | 9036.6254 | 7513.6151 | 4344.4712 | 4205.0877 | 3962.0871
Heating Fuel Deferred from Stoves (GHFE/Year) | 186.0205 | 186.025 | 253.3379 | 253.3344 | 913.232 | 913.2284 | 913.2324 | 1493.7748 | 3568.6159 | 4595.7546 | 5964.8549 | 11147.8688 | 12884.7823 | 17205.6529
Cost
Fixed Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Cost | 0 | 85000 | 1050000 | 1135000 | 1550000 | 1635000 | 1670000 | 2500000 | 2550000 | 3500000 | 4200000 | 4800000 | 5300000 | 6300000
Total Cost | 0 | 85000 | 1050000 | 1135000 | 1550000 | 1635000 | 1670000 | 2500000 | 2550000 | 3500000 | 4200000 | 4800000 | 5300000 | 6300000
Generation
Total Diesel Generation | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278
Total Solar Generation | 0 | 0 | 200 | 200 | 300 | 300 | 300 | 300 | 500 | 500 | 500 | 200 | 300 | 500
Total Wind Generation | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0% | 0 | #VALUE! | 100 | 200 | 500 | 500 | 500
Overall Diesel Efficiency | 34.95% | 34.98% | 32.31% | 32.3% | 30.51% | 30.53% | 30.53% | 27.96% | 28.48% | 25.91% | 22.18% | 11.56% | 11.11% | 10.28%
Overall Diesel Utilization | 58.79% | 58.81% | 51.92% | 51.95% | 49.02% | 49.1% | 49.1% | 40.49% | 45.99% | 37.72% | 28.3% | 15.03% | 14.58% | 13.47%
Solar Generated
Min | 0 | 0 | 4442778.12 | 4442778.12 | 6058443.35 | 6058443.35 | 6058443.35 | 6058443.35 | 8002798.36 | 8002798.36 | 8002798.36 | 4442778.12 | 6058443.35 | 8002798.36
Max | 0 | 0 | 4442778.12 | 4442778.12 | 6058443.35 | 6058443.35 | 6058443.35 | 6058443.35 | 8002798.36 | 8002798.36 | 8002798.36 | 4442778.12 | 6058443.35 | 8002798.36
Average | 0 | 0 | 4442778.12 | 4442778.12 | 6058443.35 | 6058443.35 | 6058443.35 | 6058443.35 | 8002798.36 | 8002798.36 | 8002798.36 | 4442778.12 | 6058443.35 | 8002798.36
Total | 0 | 0 | 4442778.12 | 4442778.12 | 6058443.35 | 6058443.35 | 6058443.35 | 6058443.35 | 8002798.36 | 8002798.36 | 8002798.36 | 4442778.12 | 6058443.35 | 8002798.36
Solar Spilled
Min | 0 | 0 | 79408.48 | 79408.48 | 724836.55 | 724836.55 | 724836.55 | 724836.55 | 3302668.13 | 3302668.13 | 3302668.13 | 79408.48 | 724836.55 | 3302668.13
Max | 0 | 0 | 79408.48 | 79408.48 | 724836.55 | 724836.55 | 724836.55 | 724836.55 | 3302668.13 | 3302668.13 | 3302668.13 | 79408.48 | 724836.55 | 3302668.13
Average | 0 | 0 | 79408.48 | 79408.48 | 724836.55 | 724836.55 | 724836.55 | 724836.55 | 3302668.13 | 3302668.13 | 3302668.13 | 79408.48 | 724836.55 | 3302668.13
Total | 0 | 0 | 79408.48 | 79408.48 | 724836.55 | 724836.55 | 724836.55 | 724836.55 | 3302668.13 | 3302668.13 | 3302668.13 | 79408.48 | 724836.55 | 3302668.13
Wind Generated
Min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6281142.48 | 0 | 5910534.72 | 11413918.51 | 24078887.54 | 22757066.78 | 21519378.29
Max | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6281142.48 | 0 | 5910534.72 | 11413918.51 | 24078887.54 | 22757066.78 | 21519378.29
Average | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6281142.48 | 0 | 5910534.72 | 11413918.51 | 24078887.54 | 22757066.78 | 21519378.29
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6281142.48 | 0 | 5910534.72 | 11413918.51 | 24078887.54 | 22757066.78 | 21519378.29
Wind Spilled
Min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583556.91 | 0 | 1014623.03 | 2360988.22 | 10644092.23 | 11681121.67 | 13287213.75
Max | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583556.91 | 0 | 1014623.03 | 2360988.22 | 10644092.23 | 11681121.67 | 13287213.75
Average | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583556.91 | 0 | 1014623.03 | 2360988.22 | 10644092.23 | 11681121.67 | 13287213.75
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583556.91 | 0 | 1014623.03 | 2360988.22 | 10644092.23 | 11681121.67 | 13287213.75
Weight
Fixed Weight | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Variable Weight | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Weight | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0
Volume
Fixed Volume | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0 | 0 | 0
Variable Volume | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Volume | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Load | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0
Aggregated | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Min | 57% | 57% | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57
Average | 17951% | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51
Max | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52
Tier (Only)
Load Service
Priority
Overall
Overall Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Load Served | 39311909.45 | 39311904.46 | 39311909.83 | 39311904.79 | 39311900.62 | 39311912 | 39311925.32 | 39311902.04 | 39311912.32 | 39311907.27 | 39311901.76 | 39311915.84 | 39311919.65 | 39311914.47
Total Load Not Served | 29.34 | 34.32 | 28.95 | 33.99 | 38.16 | 26.78 | 13.46 | 36.74 | 26.46 | 31.51 | 37.02 | 22.94 | 19.13 | 24.31
Post-Startup
Post-Startup Energy Availability | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
DBT Occurrences w/ Post-Startup Load Loss | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Total Post-Startup Load Served | 39311909.45 | 39311901.18 | 39311909.83 | 39311901.5 | 39311900.62 | 39311908.72 | 39311921.69 | 39311899.07 | 39311912.32 | 39311904.3 | 39311898.62 | 39311912.38 | 39311916.19 | 39311911.01
Total Post-Startup Load Not Served | 28.68 | 33.03 | 28.3 | 32.71 | 37.5 | 25.49 | 12.52 | 35.14 | 25.81 | 29.91 | 35.59 | 21.83 | 18.03 | 23.2
Startup Time
Min | 0.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Max | 0.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Average | 0.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Renewable Penetration
Min | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Max | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Average | 0% | 0% | 15.52% | 15.52% | 20.79% | 20.79% | 20.79% | 37.08% | 26.82% | 41.75% | 55.37% | 76.05% | 76.87% | 78.97%
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 0.00% | 0% | 0% | 50.9% | 50.9% | 50.9% | 50.9% | 50.9% | 4.54% | 50.9% | 3.95% | 4.27% | 4.07% | 4.28% | 3.95%
<= 25.00% | 0% | 0% | 26.99% | 26.99% | 21.92% | 21.92% | 21.92% | 41.34% | 16.69% | 39.19% | 17.34% | 11.19% | 10.61% | 9.66%
<= 50.00% | 0% | 0% | 9.41% | 9.41% | 8.69% | 8.69% | 8.69% | 28.29% | 7.73% | 25.31% | 25.37% | 7.5% | 7.06% | 6.21%
<= 75.00% | 0% | 0% | 6.34% | 6.34% | 5.8% | 5.8% | 5.8% | 8.51% | 4.78% | 7.81% | 20.51% | 9.79% | 9.28% | 8.55%
<= 100.00% | 0% | 0% | 6.35% | 6.35% | 12.69% | 12.69% | 12.69% | 17.32% | 19.9% | 23.74% | 32.51% | 67.45% | 68.78% | 71.63%
<= 110.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 120.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 130.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 140.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Diesel Fuel Use
Min | 292540654 | 2924399.56 | 2629401.86 | 2628948.84 | 2506020.72 | 2506049.2 | 2505799.74 | 2082248.52 | 2355091.42 | 1956852.04 | 1598948.13 | 865763.35 | 840021.02 | 782983.25
Max | 2925406.54 | 2924399.56 | 2629401.86 | 2628948.84 | 2506020.72 | 2506049.2 | 2505799.74 | 2082248.52 | 2355091.42 | 1956852.04 | 1598948.13 | 865763.35 | 840021.02 | 782983.25
Average | 2925406.54 | 2924399.56 | 2629401.86 | 2628948.84 | 2506020.72 | 2506049.2 | 2505799.74 | 2082248.52 | 2355091.42 | 1956852.04 | 1598948.13 | 865763.35 | 840021.02 | 782983.25
Natural Gas Use
Min | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Max | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Average | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Spinning Reserve
Min | 2.23% | 2.23% | 5.06% | 5.06% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Max | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Average | 40.39% | 40.41% | 48.05% | 47.99% | 51.29% | 51.22% | 51.24% | 59.81% | 54.8% | 62.6% | 72.09% | 85.45% | 85.83% | 87.06%
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 0.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.01% | 0.01% | 0.02% | 0.03% | 0.05% | 0.05% | 0.08%
<= 5.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 10.00% | 0.05% | 0.05% | 0.07% | 0.07% | 0.06% | 0.06% | 0.06% | 0.01% | 0.03% | 0.01% | 0% | 0% | 0% | 0%
<= 15.00% | 0.41% | 0.41% | 0.39% | 0.39% | 0.36% | 0.37% | 0.37% | 0.09% | 0.33% | 0.08% | 0.05% | 0.02% | 0.01% | 0.01%
<= 20.00% | 2.59% | 2.5% | 2.52% | 2.56% | 2.3% | 2.29% | 2.32% | 0.79% | 2.11% | 0.73% | 0.36% | 0.17% | 0.18% | 0.15%
<= 25.00% | 6.07% | 5.94% | 5.2% | 5.31% | 4.88% | 4.88% | 0.0489 | 1.95% | 0.0475 | 0.0191 | 0.0109 | 0.58% | 0.64% | 0.56%
<= 30.00% | 10.34% | 0.1024 | 0.0845 | 0.0855 | 0.0799 | 0.0806 | 0.0803 | 0.0343 | 0.0752 | 0.0333 | 0.0198 | 1.27% | 1.37% | 1.26%
<= 40.00% | 0.2646 | 0.2695 | 0.2173 | 0.2164 | 0.2048 | 0.2052 | 20.45% | 0.1115 | 19.41% | 10.63% | 5.49% | 3.85% | 3.98% | 3.7%
<= 50.00% | 0.3385 | 33.61% | 23.96% | 23.88% | 22.73% | 22.83% | 22.87% | 19.81% | 21.39% | 18.44% | 8.2% | 5.01% | 4.85% | 4.44%
<= 75.00% | 20.2% | 20.27% | 26.03% | 25.97% | 23.9% | 23.76% | 23.78% | 39.38% | 20.86% | 35.72% | 38.18% | 14.33% | 13.38% | 12.07%
<= 100.00% | 0.02% | 0.02% | 11.65% | 11.63% | 17.29% | 17.24% | 17.24% | 23.39% | 23.59% | 29.13% | 44.62% | 74.72% | 75.54% | 77.73%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Diesel Gen Set Data
JD 6619 Run Time (hours/year) | 3322.3356 | 3226.924 | 3669.0508 | 3681.3104 | 3528.7152 | 3602.9676 | 3553.7324 | 3062.6636 | 3558.0184 | 3032.066 | 3114.0468 | 3243.762 | 3261.1744 | 3230.3344
CAT 3406 Run Time (hours/year) | 6685.1132 | 6786.7444 | 6090.5352 | 6034.9972 | 6242.7016 | 6292.4384 | 6248.4824 | 5765.9304 | 6497.5 | 5653.9376 | 4976.6416 | 5013.62 | 4993.588 | 5044.4804
SD 60 Run Time (hours/year) | 591.6576 | 811.4992 | 385.388 | 383.9804 | 461.5624 | 362.2188 | 454.2052 | 512.9636 | 477.5096 | 571.0612 | 1156.6372 | 1168.2304 | 1135.4352 | 1137.5476
CMS K19G2 Run Time (hours/year) | 2.5584 | 0.0088 | 9.8504 | 16.422 | 9.4452 | 0.0088 | 0.01 | 11.58 | 8.0496 | 2.7144 | 109.7808 | 99.158 | 109.896 | 120.4944
Total Run Time | 10601.6648 | 10825.1764 | 10154.8244 | 10116.71 | 10242.4244 | 10257.6336 | 10256.43 | 9353.1376 | 10541.0776 | 9259.7792 | 9357.1064 | 9524.7704 | 9500.0936 | 9532.8568
JD 6619 Run Time (hours) | 83058.39 | 80673.1 | 91726.27 | 92032.76 | 88217.88 | 90074.19 | 88843.31 | 76566.59 | 88950.46 | 75801.65 | 77851.17 | 81094.05 | 81529.36 | 80758.36
CAT 3406 Run Time (hours) | 167127.83 | 169668.61 | 152263.38 | 150874.93 | 156067.54 | 157310.96 | 156212.06 | 144148.26 | 162437.5 | 141348.44 | 124416.04 | 125340.5 | 124839.7 | 126112.01
SD 60 Run Time (hours) | 14791.44 | 20287.48 | 9634.7 | 9599.51 | 11539.06 | 9055.47 | 11355.13 | 12824.09 | 11937.74 | 14276.53 | 28915.93 | 29205.76 | 28385.88 | 28438.69
CMS K19G2 Run Time (hours) | 63.96 | 0.22 | 246.26 | 410.55 | 236.13 | 0.22 | 0.25 | 289.5 | 201.24 | 67.86 | 2744.52 | 2478.95 | 2747.4 | 3012.36
Total Run Time | 265041.62 | 270629.41 | 253870.61 | 252917.75 | 256060.61 | 256440.84 | 256410.75 | 233828.44 | 263526.94 | 231494.48 | 233927.66 | 238119.26 | 237502.34 | 238321.42
Assumptions
Horizon (years) | 25
Nominal Discount Rate | 3%
Load Inflation Rate | 1%
Fuel Cost Adjustment | 1
Heating fuel cost ($/gal) | 7.99
Diesel oil cost ($/gal) | 7.1633
HHV (Btu/gallon) | 134000
Conversion (kWh/Btu) | 0.00029307
Baseline total fuel use (gal/year) | 186075.5898
Baseline Gen O&M net present cost | -2655676.211
Baseline diesel fuel net present cost | -13815874.8773
Baseline heating fuel net present cost | -6752037.5899
Baseline total net present cost | 21141875662.7895
Energy Efficiency Cost Electrical Curve | 0.1493
Energy Efficiency Cost Electrical Curve | -0.9009
Energy Efficiency Cost Electrical Curve | 16.515
Energy Efficiency Cost Thermal Curve | 0.1123
Energy Efficiency Cost Thermal Curve | -0.6774
Energy Efficiency Cost Thermal Curve | 12.418
Baseline electrical load (kWh/year) | 1747196.0752
Baseline thermal load (kWh/year) | 2813162.6652
EE electrical load(kWh/year) | 1572476.378
EE thermal load(kWh/year) | 1828555.68
Assumed replacement usage (hours) | 80000
Gen replacement curve ($/kW) | 410.53
Gen replacement curve ($) | 105.26
202kW Gen O&M | 15.7808
314kW Gen O&M | 16.4528
365kW Gen O&M | 16.7588
397kW Gen O&M | 17.1422
Wind Replacement cost (First turbine) | 560000
Wind O&M Cost ($/kWh) | 17500
Solar O&M Cost ($/hour/100kW) | 0.54
EE electrical load reduction (%) | 0.1
EE thermal load reduction (%) | 0.35
EE electrical load reduction cost ($/kWh/year) | 0.22436
EE thermal load reduction cost ($/kWh/year) | 1.3964
EE electrical load reduction cost ($/kWh/year) | -39200.1328
EE thermal load reduction cost ($/kWh/year) | -1374920.1102 | -1414120.243
Financial calculations
RE Purchase Cost | 0 | -85000 | -1050000 | -1135000 | -1550000 | -1635000 | -1670000 | -2500000 | -2550000 | -3500000 | -4200000 | -4800000 | -5300000 | -6300000
Stove Cost | 0 | 0 | -10181.3 | -10181.3 | -11654.88 | -11654.88 | -11654.88 | -12987.2 | -17540.34 | -19856.83 | -22930.72 | -34482.88 | -38324.11 | -47876.44
kW of Stoves | 0 | 0 | 0.3626 | 0.3626 | 3.3098 | 3.3098 | 3.3098 | 5.9744 | 15.0807 | 19.7137 | 25.8614 | 48.9658 | 56.6482 | 75.7529
# of Stoves | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 5 | 9 | 10 | 13
Gen Replacement Cost (per year)
JD 6619 | -3448.2654 | -3349.2373 | -3808.1225 | -3820.8468 | -3662.4676 | -3739.5345 | -3688.4331 | -3178.7508 | -3692.8815 | -3146.9934 | -3232.0816 | -3366.7136 | -3384.786 | -3352.777
CAT 3406 | -10780.7211 | -10944.6162 | -9821.8772 | -9732.3141 | -10067.2678 | -10147.4756 | -10076.5901 | -9298.4046 | -10478.1674 | -9117.7999 | -8025.5612 | -8085.1942 | -8052.8897 | -8134.9611
SD 60 | -1108.9787 | -1521.0407 | -722.3554 | -719.7171 | -865.1336 | -678.928 | -851.3435 | -961.4779 | -895.0244 | -1070.3736 | -2167.9532 | -2189.683 | -2128.213 | -2132.1724
CMS | -5.2155 | -0.017939 | -20.0807 | -33.4774 | -19.2547 | -0.017939 | -0.020386 | -23.6067 | -16.4097 | -5.5335 | -223.7959 | -202.1406 | -224.0308 | -245.6364
New Small (100kW) Gen (purchase) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Gen O&M Cost (per year)
JD 6619 | -52428.9475 | -50923.2809 | -57900.3734 | -58093.8391 | -55685.7724 | -56857.531 | -56080.5626 | -48331.1286 | -56148.1989 | -47848.2755 | -49141.994 | -51188.9972 | -51463.7779 | -50977.0996
CAT 3406 | -109988.4962 | -111660.6089 | -100206.053 | -99292.3002 | -102709.6087 | -103527.9159 | -102804.7188 | -94865.4114 | -106901.7431 | -93022.8218 | -81879.4401 | -82487.8365 | -82158.255 | -82995.5749
SD 60 | -9915.4418 | -13599.7122 | -6458.6211 | -6435.0315 | -7735.2089 | -6070.3343 | -7611.9114 | -8596.6287 | -8002.464 | -9570.2719 | -19383.7937 | -19578.0812 | -19028.4747 | -19063.8758
CMS | -43.8567 | -0.15085 | -168.858 | -281.5099 | -161.9119 | -0.15085 | -0.17142 | -198.5072 | -137.9882 | -46.5309 | -1881.8893 | -1699.7907 | -1883.8641 | -2065.5445
Deasil Fuel use (Gal/year) | 117033.6 | 116946 | 105207.6 | 105120 | 100214.4 | 100214.4 | 100214.4 | 83307.6 | 94170 | 78314.4 | 63948 | 34602 | 33638.4 | 31360.8
Heating Fuel use (Gal/year) | 33778.5354 | 33778.2254 | 34710.9554 | 34710.8754 | 34539.5854 | 34539.7754 | 34539.6054 | 35490.8654 | 32496.2054 | 32929.5054 | 33083.4154 | 31069.5454 | 29472.0154 | 25394.1454
Total Fuel usage (Gal/year) | 150812.1354 | 150724.2254 | 139918.5554 | 139830.8754 | 134753.9854 | 134754.1754 | 134754.0054 | 118798.4654 | 126666.2054 | 111243.9054 | 97031.4154 | 65671.5454 | 63110.4154 | 56754.9454
New Wind Turbines (#) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 5 | 5 | 5
New 100kW Solar Fields (#) | 0 | 0 | 2 | 2 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 2 | 3 | 5
Wind Replacement Cost (per replacement) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -560000 | 0 | -560000 | -1092000 | -2520000 | -2520000 | -2520000
Wind Replacement NPV (Turbines are replaced every 20 years: this means that the first replacement is out of the time horizon for this analysis and so the replacement cost is not used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Replacement NPV (converter only after 10 years) | 0 | 0 | -126423.7234 | -126423.7234 | -189635.5851 | -189635.5851 | -189635.5851 | -189635.5851 | -316059.3085 | -316059.3085 | -316059.3085 | -126423.7234 | -189635.5851 | -316059.3085
Wind O&M Cost per year ($/year) | 0 | 0 | -34562.5 | -34562.5 | -51187.5 | -51187.5 | -51187.5 | -51187.5 | -83125 | -83125 | -83125 | -34562.5 | -51187.5 | -83125
Solar O&M Cost per year ($/year) | 0 | 0 | -9460.8 | -9460.8 | -14191.2 | -14191.2 | -14191.2 | -14191.2 | -23652 | -23652 | -23652 | -9460.8 | -14191.2 | -23652
Gen + Wind + Solar O&M + Genorator Replacement Cost
Year
1 | -187719.9229 | -191998.6651 | -223129.6414 | -222432.3361 | -246285.3256 | -246400.5881 | -246492.4514 | -230832.6158 | -293049.8772 | -270605.6006 | -272713.5091 | -212821.737 | -233702.9911 | -275744.6417
2 | -176944.0314 | -180977.1563 | -210321.0872 | -209663.8101 | -232147.5404 | -232256.1863 | -232342.7763 | -217581.8794 | -276227.6154 | -255071.7321 | -257058.638 | -200604.8986 | -220287.4834 | -259915.7713
3 | -171790.3217 | -175705.977 | -204195.2303 | -203557.0972 | -225385.9616 | -225491.443 | -225575.5109 | -211244.5431 | -268182.1509 | -247642.4583 | -249571.4932 | -194762.0375 | -213871.3431 | -252345.409
4 | -166786.7201 | -170588.3272 | -198247.7964 | -197628.2497 | -218821.3219 | -218923.7311 | -219005.3504 | -205091.7894 | -260371.0203 | -240429.5712 | -242302.4206 | -189089.3568 | -207642.0807 | -244995.5427
5 | -161928.8545 | -165619.7351 | -192473.5887 | -191872.0871 | -212447.8853 | -212547.3117 | -212626.5538 | -199118.2421 | -252787.3983 | -233426.7682 | -235245.0685 | -183581.8998 | -201594.2531 | -237859.7502
6 | -157212.4801 | -160795.8593 | -186867.5619 | -186283.5797 | -206260.0829 | -206356.6133 | -206433.5474 | -193318.6817 | -245424.6585 | -226627.9303 | -228393.2704 | -178234.8542 | -195722.5758 | -230931.7963
7 | -152633.4758 | -156112.4848 | -181424.8174 | -180857.8443 | -200252.5076 | -200346.2265 | -200420.9198 | -187688.0405 | -238276.3675 | -220027.1168 | -221741.0392 | -173043.5478 | -190021.9183 | -224205.6275
8 | -148187.8406 | -151565.5192 | -176140.5994 | -175590.1401 | -194419.9103 | -194510.8996 | -194583.4173 | -182221.3985 | -231336.2791 | -213618.56 | -215282.5624 | -168003.4444 | -184487.2993 | -217675.3665
9 | -143871.6899 | -147150.9895 | -171010.2907 | -170475.8642 | -188757.1945 | -188845.5336 | -188915.9391 | -176913.9792 | -224598.3293 | -207396.6602 | -209012.1965 | -163110.1402 | -179113.8828 | -211335.3073
10 | -139681.2523 | -142865.0384 | -166029.4084 | -165510.5478 | -183259.4121 | -183345.1782 | -183413.5331 | -171761.1448 | -218056.6304 | -201355.9807 | -202924.4626 | -158359.3594 | -173896.9736 | -205179.91
11 | -135612.8663 | -138703.9208 | -161193.6004 | -160689.8522 | -177921.7593 | -178005.0274 | -178071.3914 | -166758.393 | -211705.4664 | -195491.2434 | -197014.0414 | -153746.9509 | -168832.0132 | -199203.7961
12 | -131662.977 | -134664.0007 | -156498.6412 | -156009.5653 | -172739.5722 | -172820.4149 | -172884.846 | -161901.3524 | -205539.2877 | -189797.3237 | -191275.7683 | -149268.8844 | -163914.5759 | -193401.7438
13 | -127828.133 | -130741.7483 | -151940.4283 | -151465.5973 | -167708.3225 | -167786.8106 | -167849.365 | -157185.7791 | -199552.7065 | -184269.2463 | -185704.6294 | -144921.247 | -159140.365 | -187768.6833
14 | -124104.9835 | -126933.7362 | -147514.9789 | -147053.978 | -162823.6141 | -162899.8161 | -162960.5486 | -152607.5525 | -193740.4918 | -178902.1809 | -180295.7567 | -140700.2398 | -154505.2087 | -182299.6925
15 | -120490.2753 | -123236.6371 | -143218.4262 | -142770.8524 | -158081.1787 | -158155.1613 | -158214.1248 | -148162.6723 | -188097.5648 | -173691.4378 | -175044.424 | -136602.1745 | -150005.057 | -176989.9927
16 | -116980.8498 | -119647.2205 | -139047.0157 | -138612.4781 | -153476.8725 | -153548.7003 | -153605.9464 | -143847.2547 | -182618.995 | -168632.4639 | -169946.0427 | -132623.4704 | -145635.9777 | -171834.9444
17 | -113573.6405 | -116162.35 | -134997.1026 | -134575.2214 | -149006.6724 | -149076.408 | -149131.9868 | -139657.5288 | -177299.9951 | -163720.8387 | -164996.158 | -128760.6509 | -141394.1531 | -166830.0431
18 | -110265.6704 | -112778.9806 | -131065.1482 | -130655.5548 | -144666.6722 | -144734.3767 | -144788.3367 | -135589.8338 | -172135.9176 | -158952.2706 | -160190.4446 | -125010.3407 | -137275.8768 | -161970.9156
19 | -107054.049 | -109494.1559 | -127247.7167 | -126850.0532 | -140453.0798 | -140518.8124 | -140571.2007 | -131640.6153 | -167122.2501 | -154322.5928 | -155524.7035 | -121369.2628 | -133277.5503 | -157253.3162
20 | -103935.9699 | -106305.0057 | -123541.4725 | -123155.3915 | -136362.2134 | -136426.0314 | -136476.8939 | -127806.4227 | -162254.6118 | -149827.76 | -150994.8578 | -117834.2357 | -129395.6799 | -152673.1225
Total Gen O&M + Replacement Cost | -2798266.0038 | -2862047.5076 | -3326104.5525 | -3315710.1004 | -3671277.0994 | -3672995.2707 | -3674364.64 | -3440929.7192 | -4368377.6137 | -4033809.7363 | -4106389.7471 | -3213606.9928 | -3524875.5188 | -4151573.6328
Diesel Fuel Cost
Year
1 | -838350.688 | -837723.18 | -753637.108 | -753009.6 | -717869.152 | -717869.152 | -717869.152 | -596760.108 | -674571.1 | -560992.152 | -458080.84 | -247865.66 | -240963.072 | -224647.864
2 | -790225.9289 | -789634.4425 | -710375.255 | -709783.7685 | -676660.526 | -676660.526 | -676660.526 | -562503.6365 | -635847.9593 | -528788.9075 | -431785.1258 | -233637.1571 | -227130.8059 | -211752.1576
3 | -767209.6397 | -766635.381 | -689684.7136 | -689110.4549 | -656951.967 | -656951.967 | -656951.967 | -546120.0355 | -617328.1158 | -513387.2889 | -419208.86 | -226832.1914 | -220515.3456 | -205584.619
4 | -744863.7279 | -744306.1952 | -669596.8093 | -669039.2766 | -637817.4437 | -637817.4437 | -637817.4437 | -530213.6267 | -599347.6852 | -498434.261 | -406998.8932 | -220225.4285 | -214092.5685 | -199596.7175
5 | -723168.6679 | -722627.374 | -650093.9896 | -649552.6957 | -619240.2366 | -619240.2366 | -619240.2366 | -514770.5113 | -581890.9566 | -483916.7583 | -395144.5565 | -213811.0957 | -207856.8626 | -193783.2209
6 | -702105.5028 | -701579.9747 | -631159.2132 | -630633.6851 | -601204.1132 | -601204.1132 | -601204.1132 | -499777.1955 | -564942.6763 | -469822.0954 | -383635.4918 | -207583.588 | -201802.7792 | -188139.0494
7 | -681655.8279 | -681145.6065 | -612775.9351 | -612265.7137 | -583693.3137 | -583693.3137 | -583693.3137 | -485220.5781 | -548488.0352 | -456137.9567 | -372461.6425 | -201537.4641 | -195925.0284 | -182659.2713
8 | -661801.7747 | -661306.4141 | -594928.0924 | -594432.7318 | -566692.5376 | -566692.5376 | -566692.5376 | -471087.9399 | -532512.6555 | -442852.3852 | -361613.2452 | -195667.4409 | -190218.4742 | -177339.0983
9 | -642525.9949 | -642045.0622 | -577600.0897 | -577119.1571 | -550186.9297 | -550186.9297 | -550186.9297 | -457366.932 | -517002.5782 | -429953.772 | -351080.8205 | -189968.3892 | -184678.1303 | -172173.8819
10 | -623811.6455 | -623344.7206 | -560776.7861 | -560309.8612 | -534162.0677 | -534162.0677 | -534162.0677 | -444045.565 | -501944.2507 | -417430.8466 | -340855.1656 | -184435.3293 | -179299.1556 | -167159.1086
11 | -605642.3743 | -605189.0491 | -544443.4817 | -543990.1565 | -518603.9492 | -518603.9492 | -518603.9492 | -431112.199 | -487324.5152 | -405272.6666 | -330927.3452 | -179063.4265 | -174076.8501 | -162290.3967
12 | -588002.3051 | -587562.1836 | -528585.9045 | -528145.783 | -503498.9798 | -503498.9798 | -503498.9798 | -418555.5331 | -473130.5973 | -393468.6084 | -321288.6847 | -173847.9869 | -169006.6506 | -157563.4919
13 | -570876.0244 | -570448.722 | -513190.1986 | -512762.8961 | -488833.961 | -488833.961 | -488833.961 | -406364.5952 | -459350.0945 | -382008.3576 | -311930.7618 | -168784.4533 | -164084.1268 | -152974.264
14 | -554248.5674 | -553833.7106 | -498242.9112 | -497828.0545 | -474596.0786 | -474596.0786 | -474596.0786 | -394528.7332 | -445970.9655 | -370881.9006 | -302845.3998 | -163868.4013 | -159304.9774 | -148518.7029
15 | -538105.4052 | -537702.6317 | -483730.9818 | -483328.2083 | -460772.8919 | -460772.8919 | -460772.8919 | -383037.605 | -432981.5199 | -360079.5152 | -294024.66 | -159095.5352 | -154665.0266 | -144192.9155
16 | -522432.4322 | -522041.39 | -469641.7299 | -469250.6876 | -447352.3222 | -447352.3222 | -447352.3222 | -371881.17 | -420370.4077 | -349591.7623 | -285460.835 | -154461.6847 | -150160.22 | -139993.1218
17 | -507215.9536 | -506836.301 | -455962.8445 | -455583.1919 | -434322.6429 | -434322.6429 | -434322.6429 | -361049.6796 | -408126.6094 | -339409.4779 | -277146.4417 | -149962.8007 | -145786.6214 | -135915.6522
18 | -492442.6734 | -492074.0786 | -442682.3733 | -442313.7785 | -421672.4689 | -421672.4689 | -421672.4689 | -350533.6695 | -396239.4266 | -329523.765 | -269074.2153 | -145594.9521 | -141540.4091 | -131956.9439
19 | -478099.6829 | -477741.8239 | -429788.712 | -429430.8529 | -409390.7465 | -409390.7465 | -409390.7465 | -340323.951 | -384698.4724 | -319925.9854 | -261237.1022 | -141354.3224 | -137417.8729 | -128113.5378
20 | -464174.4495 | -463827.0135 | -417270.5942 | -416923.1582 | -397466.7441 | -397466.7441 | -397466.7441 | -330411.6029 | -373493.6625 | -310607.7529 | -253628.2546 | -137237.2062 | -133415.4106 | -124382.0755
Total Diesel Fuel Cost | -12496959.2662 | -12487605.2547 | -11234167.7236 | -11224813.7121 | -10700989.0722 | -10700989.0722 | -10700989.0722 | -8895664.8669 | -10055562.2838 | -8362486.2155 | -6828428.3415 | -3694834.5136 | -3591940.3879 | -3348736.0908
Heating Fuel Cost
Year
1 | -269890.4974 | -269888.0205 | -277340.5332 | -277339.8941 | -275971.2869 | -275972.805 | -275971.4467 | -283572.0141 | -259644.6807 | -263106.7477 | -264336.4887 | -248245.6673 | -235481.4026 | -202899.2213
2 | -254397.6788 | -254395.3441 | -261420.0521 | -261419.4496 | -260129.4061 | -260130.8371 | -260129.5567 | -267293.8205 | -244740.0139 | -248003.3441 | -249162.4929 | -233995.3505 | -221963.8068 | -191251.976
3 | -246988.0377 | -246985.771 | -253805.8758 | -253805.2909 | -252552.8215 | -252554.2107 | -252552.9677 | -259508.5636 | -237611.664 | -240779.9457 | -241905.3329 | -227179.9519 | -215498.8416 | -185681.5301
4 | -239794.2113 | -239792.0106 | -246413.4717 | -246412.9038 | -245196.9141 | -245198.2629 | -245197.056 | -251950.0617 | -230690.9359 | -233766.9376 | -234859.5465 | -220563.0601 | -209222.1763 | -180273.3302
5 | -232809.9139 | -232807.7773 | -239236.3802 | -239235.8289 | -238055.2564 | -238056.5659 | -238055.3942 | -244611.7104 | -223971.7824 | -226958.1918 | -228018.9772 | -214138.8933 | -203128.3265 | -175022.6507
6 | -226029.0426 | -226026.9683 | -232268.3303 | -232267.7951 | -231121.6081 | -231122.8795 | -231121.7419 | -237487.0975 | -217448.3325 | -220347.7591 | -221377.6478 | -207901.8382 | -197211.9675 | -169924.9036
7 | -219445.6725 | -219443.6585 | -225503.2333 | -225502.7137 | -224389.9108 | -224391.1451 | -224390.0407 | -230569.9976 | -211114.8859 | -213929.8632 | -214929.7551 | -201846.4448 | -191467.9296 | -164975.6345
8 | -213054.0509 | -213052.0957 | -218935.178 | -218934.6735 | -217854.2823 | -217855.4807 | -217854.4085 | -223854.3666 | -204965.9086 | -207698.8963 | -208669.6652 | -195967.4222 | -185891.1938 | -160170.519
9 | -206848.5931 | -206846.6948 | -212558.4252 | -212557.9354 | -211509.012 | -211510.1755 | -211509.1344 | -217334.3365 | -198996.0278 | -201649.4139 | -202591.9079 | -190259.6332 | -180476.8871 | -155505.3582
10 | -200823.8768 | -200822.0338 | -206367.4031 | -206366.9276 | -205348.5553 | -205349.6849 | -205348.6742 | -211004.2102 | -193200.027 | -195776.13 | -196691.1727 | -184718.0905 | -175220.2788 | -150976.0759
11 | -194974.6377 | -194972.8483 | -200356.7021 | -200356.2404 | -199367.5294 | -199368.6261 | -199367.6449 | -204858.4565 | -187572.8417 | -190073.9126 | -190962.3036 | -179337.9519 | -170116.7755 | -146578.7145
12 | -189295.7648 | -189294.0275 | -194521.07 | -194520.6217 | -193560.7082 | -193561.7729 | -193560.8203 | -198891.7053 | -182109.5551 | -184537.7792 | -185400.2948 | -174114.5164 | -165161.918 | -142309.4316
13 | -183782.2959 | -183780.6092 | -188855.4078 | -188854.9725 | -187923.0176 | -187924.0514 | -187923.1265 | -193098.743 | -176805.3933 | -179162.8924 | -180000.2862 | -169043.2198 | -160351.3767 | -138164.4967
14 | -178429.4135 | -178427.776 | -183354.7648 | -183354.3423 | -182449.5317 | -182450.5353 | -182449.6373 | -187474.5078 | -171655.7216 | -173944.5558 | -174757.5594 | -164119.6309 | -155680.9482 | -134140.288
15 | -173232.4403 | -173230.8504 | -178014.3348 | -178013.9245 | -177135.4677 | -177136.4421 | -177135.5702 | -182014.0852 | -166656.0404 | -168878.2095 | -169667.5334 | -159339.4475 | -151146.5517 | -130233.2893
16 | -168186.8352 | -168185.2917 | -172829.4512 | -172829.0529 | -171976.1822 | -171977.1282 | -171976.2818 | -176712.7041 | -161801.981 | -163959.4267 | -164725.7606 | -154698.4927 | -146744.2249 | -126440.0867
17 | -163288.1895 | -163286.691 | -167795.5837 | -167795.197 | -166967.1672 | -166968.0857 | -166967.2639 | -171565.7321 | -157089.3019 | -159183.9094 | -159927.9229 | -150192.7114 | -142470.1213 | -122757.3658
18 | -158532.2228 | -158530.7679 | -162908.3337 | -162907.9583 | -162104.0458 | -162104.9375 | -162104.1397 | -166568.672 | -152513.8854 | -154547.4849 | -155269.8281 | -145818.1664 | -138320.5061 | -119181.9085
19 | -153914.7795 | -153913.3669 | -158163.4308 | -158163.0663 | -157382.5687 | -157383.4345 | -157382.6599 | -161717.1573 | -148071.7334 | -150046.1018 | -150747.4059 | -141571.0353 | -134291.7535 | -115710.5908
20 | -149431.8247 | -149430.4533 | -153556.7289 | -153556.375 | -152798.6104 | -152799.451 | -152798.6989 | -157006.9488 | -143758.9644 | -145675.827 | -146356.7048 | -137447.6071 | -130380.3432 | -112340.3794
Total Heating Fuel Cost | -4023149.9791 | -4023113.057 | -4134204.6908 | -4134195.1637 | -4113793.8824 | -4113816.5121 | -4113796.2645 | -4227094.8907 | -3870419.6769 | -3922027.3286 | -3940358.5868 | -3700499.1315 | -3510227.3296 | -3024537.7509
Total Net Present Cost | -20732495.4921 | -20871886.0623 | -21295202.2332 | -21360444.2426 | -21651470.7621 | -21738211.5632 | -21774560.6849 | -20680432.5049 | -22592079.4659 | -21568359.6619 | -20828286.947 | -16983967.4843 | -17569123.1744 | -18602903.466
Marginal Net Present Value (NPC-Baseline) | -21162608158.2816 | -21162747548.8518 | -21163170865.0227 | -21163236107.0321 | -21163527133.5516 | -21163613874.3527 | -21163650223.4744 | -21162556095.2943 | -21164467742.2553 | -21163444022.4514 | -21162703949.7365 | -21158859630.2738 | -21159444785.9639 | -21160478566.2555
Net Reduction in Imported Fuel | 18.95% | 19% | 24.81% | 24.85% | 27.58% | 27.58% | 27.58% | 36.16% | 31.93% | 40.22% | 47.85% | 64.71% | 66.08% | 69.5%
Marginal NPV = NPC - NPC(baseline) - capital investment | Highest NPV Cases
Marginal NPV (Utility Only) | 1176325.8184 | 1036898.326 | 734855.0889 | 669603.5524 | 359649.3316 | 272931.1603 | 236561.791 | 1445320.9171 | -818448.1176 | 259195.828 | 1020673.6912 | 4636685.8586 | 3865099.5966 | 2355182.0562
Marginal NPV (Heating Customers Only) | 1353967.5006 | 1354004.4227 | 1232731.4889 | 1232741.016 | 1251668.7173 | 1251646.0876 | 1251666.3352 | 1137035.389 | 1489157.4628 | 1435233.3211 | 1413828.1729 | 1642135.4682 | 1828566.0401 | 2304703.2888
Total Marginal NPV | 2530293.3189 | 2390902.7487 | 1967586.5778 | 1902344.5684 | 1611318.0489 | 1524577.2478 | 1488228.1262 | 2582356.3062 | 670709.3452 | 1694429.1492 | 2434501.8641 | 6278821.3268 | 5693665.6366 | 4659885.345
Total % ROI | 278.9% | 259.5% | 179.5% | 174.3% | 154.1% | 149.8% | 148.1% | 165.8% | 116.8% | 134.3% | 143.2% | 200.5% | 184.3% | 160%
Normalized to Energy Efficient System
Normalized NPV (Utility Only) |  | -139427.4923 | -441470.7294 | -506722.2659 | -816676.4867 | -903394.6581 | -939764.0274 | 268995.0988 | -1994773.936 | -917129.9903 | -155652.1272 | 3460360.0402 | 2688773.7782 | 1178856.2379
Normalized NPV (Heating Customers Only) |  | 36.9222 | -121236.0117 | -121226.4846 | -102298.7833 | -102321.413 | -102301.1654 | -216932.1115 | 135189.9622 | 81265.8206 | 59860.6723 | 288167.9676 | 474598.5395 | 950735.7883
Normalized Total NPV |  | -139390.5702 | -562706.7411 | -627948.7505 | -918975.27 | -1005716.0711 | -1042065.1928 | 52062.9873 | -1859583.9737 | -835864.1698 | -95791.4548 | 3748528.0079 | 3163372.3177 | 2129592.0261
Normalized % ROI |  | -63.99% | 46.92% | 45.17% | 41.15% | 38.92% | 38.03% | 102.1% | 27.57% | 76.25% | 97.73% | 177.5% | 159.3% | 133.5%
No Generator
100kW Diesel
Note on A225: Author: Already Included in Purchase Cost
Note on A234: Author: If the generator utilization is less than 30% then a new small generator is purchased (This assumes that the O&M costs for the generator set would not change as the O&M cost for the new generator would offset some of the O&M cost for the existing generator)
Note on B334: Author: NPV Values are normalized to the Baseline
Note on C334: Author: NPV Values are normalized to the Baseline
Note on D334: Author: NPV Values are normalized to the Baseline
Note on E334: Author: NPV Values are normalized to the Baseline
Note on F334: Author: NPV Values are normalized to the Baseline
Note on G334: Author: NPV Values are normalized to the Baseline
Note on H334: Author: NPV Values are normalized to the Baseline
Note on I334: Author: NPV Values are normalized to the Baseline
Note on J334: Author: NPV Values are normalized to the Baseline
Note on K334: Author: NPV Values are normalized to the Baseline
Note on L334: Author: NPV Values are normalized to the Baseline
Note on M334: Author: NPV Values are normalized to the Baseline
Note on N334: Author: NPV Values are normalized to the Baseline
Note on O334: Author: NPV Values are normalized to the Baseline
Note on A335: Author: Value of Heating Fuel Deferred - Cost of Stove System
Note on B335: Author: NPV Values are normalized to the Baseline
Note on A341: Author: Value of Heating Fuel Deferred - Cost of Stove System

## Med-EE no Stoves Detailed
Summary Results
New Solar | No Generator | SG 100 | SG 100 | No Generator | No Generator | SG 200 | SG 200 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 500 | SG 200 | SG 300 | SG 300 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | WG 100 | WG 100 | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | No Generator | WG 100 | WG 200 | WG 500 | WG 500 | WG 500 | WG 500
New Storage | No Battery | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery | No Battery | No Battery | Bat 50/50 | Bat 100/100 | No Battery | No Battery | No Battery | No Battery | Bat 50/50 | No Battery
New Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel
Energy Efficiency Cost | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899
Renewable Energy Purchase Cost | 0 | -550000 | -635000 | -950000 | -1035000 | -1050000 | -1135000 | -1550000 | -2500000 | -2550000 | -2635000 | -2670000 | -3500000 | -4200000 | -4800000 | -5300000 | -5385000 | -6300000
Stove Purchase Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Generator Purchase Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Net Reduction in Imported Fuel | 18.9% | 21.69% | 21.69% | 27.89% | 27.81% | 24.72% | 24.72% | 27.09% | 35.57% | 30.01% | 30.01% | 30.01% | 37.8% | 44.42% | 57.83% | 59.56% | 58.59% | 60.19%
Marginal NPV (Utility Only) | 1077750.0826 | 941285.194 | 780610.7702 | 2272355.0259 | 2136489.6392 | 629228.4436 | 602022.0772 | 358806.0503 | 1307461.47 | -731394.0414 | -856191.2795 | -896365.0575 | 119329.499 | 906509.2494 | 4429355.0642 | 3928397.4817 | 3596169.0946 | 2313122.3316
Marginal NPV (Heating Customers Only) | 1331860.0482 | 1282541.008 | 1282538.0989 | 1154060.8765 | 1157291.6352 | 1212759.9123 | 1212764.0345 | 1154526.1729 | 968493.3174 | 1081664.2664 | 1081676.2388 | 1081673.5129 | 909764.3973 | 728295.112 | 370585.1304 | 327493.0705 | 352904.4815 | 310262.6303
Total Marginal NPV | 2409610.1308 | 2223826.202 | 2063148.8691 | 3426415.9024 | 3293781.2744 | 1841988.3559 | 1814786.1118 | 1513332.2232 | 2275954.7875 | 350270.225 | 225484.9593 | 185308.4554 | 1029093.8963 | 1634804.3613 | 4799940.1946 | 4255890.5522 | 3949073.5761 | 2623384.9619
Total % ROI | 270.4% | 213.2% | 200.7% | 244.9% | 234.5% | 174.8% | 171.2% | 151.1% | 158.1% | 108.8% | 105.6% | 104.5% | 120.9% | 129.1% | 177.2% | 163.4% | 158.1% | 134%
Total Capital Cost | 1414119.9899 | 1964119.9899 | 2049119.9899 | 2364119.9899 | 2449119.9899 | 2464119.9899 | 2549119.9899 | 2964119.9899 | 3914119.9899 | 3964119.9899 | 4049119.9899 | 4084119.9899 | 4914119.9899 | 5655278.2499 | 6255278.2499 | 6755278.2499 | 6840278.2499 | 7755278.2499
Raw DATA
Simulation Statistics | 1 | 2 | 4 | 5 | 7 | 8 | 10 | 11 | 13 | 14 | 16 | 17 | 18 | 19 | 21 | 23 | 24 | 25
Total Sim Time | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Power Utility Statistics
Failure Statistics
Occurrences | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations")
Downtime
Min | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Max | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Average | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Total | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Thermal Load Service
Overall
Overall Energy Availability | 27.06% | 26.17% | 26.17% | 23.85% | 23.91% | 24.91% | 24.91% | 23.86% | 20.5% | 22.54% | 22.54% | 22.54% | 19.44% | 16.17% | 9.722% | 8.945% | 9.403% | 0.086344
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Total Load Served | 12368301.25 | 11961757.89 | 11961733.91 | 10902679.23 | 10929310.81 | 11386543.12 | 11386577.1 | 10906514.74 | 9373021.38 | 10305904.43 | 10306003.12 | 10305980.66 | 8888911.16 | 7393035.92 | 4444385.38 | 4089171.86 | 4298641.47 | 3947139.07
Total Load Not Served | 33345592.07 | 33752135.42 | 33752159.4 | 34811214.08 | 34784582.51 | 34327350.19 | 34327316.21 | 34807378.58 | 36340871.93 | 35407988.88 | 35407890.19 | 35407912.66 | 36824982.16 | 38320857.4 | 41269507.93 | 41624721.46 | 41415251.85 | 41766754.25
Post-Startup
Post-Startup Energy Availability
DBT Occurrences w/ Post-Startup Load Loss
Total Post-Startup Load Served | 12368301.25 | 11961757.89 | 11961733.91 | 10902679.23 | 10929310.81 | 11386543.12 | 11386577.1 | 10906514.74 | 9373021.38 | 10305904.43 | 10306003.12 | 10305980.66 | 8888911.16 | 7393035.92 | 4444385.38 | 4089171.86 | 4298641.47 | 3947139.07
Total Post-Startup Load Not Served | 33345592.07 | 33752135.42 | 33752159.4 | 34811214.08 | 34784582.51 | 34327350.19 | 34327316.21 | 34807378.58 | 36340871.93 | 35407988.88 | 35407890.19 | 35407912.66 | 36824982.16 | 38320857.4 | 41269507.93 | 41624721.46 | 41415251.85 | 41766754.25
Variable Selections
New Solar | No Generator | SG 100 | SG 100 | No Generator | No Generator | SG 200 | SG 200 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 500 | SG 200 | SG 300 | SG 300 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | WG 100 | WG 100 | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | No Generator | WG 100 | WG 200 | WG 500 | WG 500 | WG 500 | WG 500
New Storage | No Battery | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery | No Battery | No Battery | Bat 50/50 | Bat 100/100 | No Battery | No Battery | No Battery | No Battery | Bat 50/50 | No Battery
Metric Values
Purchase Cost | 0 | 550000 | 635000 | 950000 | 1035000 | 1050000 | 1135000 | 1550000 | 2500000 | 2550000 | 2635000 | 2670000 | 3500000 | 4200000 | 4800000 | 5300000 | 5385000 | 6300000
Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Diesel Fuel Used (Gal/Hour) | 13.35 | 12.71 | 12.71 | 11.27 | 11.29 | 12 | 12 | 11.44 | 9.46 | 10.75 | 10.75 | 10.75 | 8.93 | 7.35 | 4.16 | 3.75 | 3.98 | 3.6
Heating Fuel Deferred (GHFE/Year) | 12597.7331 | 12183.6483 | 12183.6239 | 11104.9238 | 11132.0494 | 11597.7633 | 11597.7979 | 11108.8304 | 9546.8908 | 10497.0788 | 10497.1793 | 10497.1564 | 9053.8003 | 7530.1766 | 4526.8287 | 4165.0259 | 4378.3812 | 4020.3584
Average Renewable Energy Spilled | 0 | 0 | 0 | 565.01 | 590.51 | 79408.48 | 79408.48 | 724836.55 | 1313588.09 | 3302668.13 | 3302668.13 | 3302668.13 | 4329053.86 | 5592241.08 | 10401360.38 | 12646025.46 | 12261919.68 | 16651739.08
Diesel Utilization | 58.95% | 55.87% | 0.5603 | 0.5224 | 0.5234 | 0.5208 | 0.5221 | 0.4922 | 41.07% | 45.74% | 46.03% | 46.1% | 38.38% | 28.7% | 16.21% | 14.38% | 15.44% | 0.1384
Heating Fuel Deferred from Waste Heat (GHFE/Year) | 12597.7331 | 12183.6483 | 12183.6239 | 11104.9238 | 11132.0494 | 11597.7633 | 11597.7979 | 11108.8304 | 9546.8908 | 10497.0788 | 10497.1793 | 10497.1564 | 9053.8003 | 7530.1766 | 4526.8287 | 4165.0259 | 4378.3812 | 4020.3584
Heating Fuel Deferred from Stoves (GHFE/Year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost
Fixed Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Cost | 0 | 550000 | 635000 | 950000 | 1035000 | 1050000 | 1135000 | 1550000 | 2500000 | 2550000 | 2635000 | 2670000 | 3500000 | 4200000 | 4800000 | 5300000 | 5385000 | 6300000
Total Cost | 0 | 550000 | 635000 | 950000 | 1035000 | 1050000 | 1135000 | 1550000 | 2500000 | 2550000 | 2635000 | 2670000 | 3500000 | 4200000 | 4800000 | 5300000 | 5385000 | 6300000
Generation
Total Diesel Generation | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278
Total Solar Generation | 0% | 10000% | 100 | 100 | 100 | 200 | 200 | 300 | 300 | 500 | 500 | 500 | 500 | 500 | 200 | 300 | 300 | 500
Total Wind Generation | 0% | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 200 | 500 | 500 | 500 | 500
Overall Diesel Efficiency | 34.99% | 34.26% | 34.3% | 33.96% | 33.96% | 32.36% | 32.36% | 30.52% | 28.16% | 28.32% | 28.43% | 28.44% | 26.14% | 22.43% | 12.16% | 10.95% | 11.55% | 0.1042
Overall Diesel Utilization | 58.95% | 55.87% | 56.03% | 52.24% | 52.34% | 52.08% | 52.21% | 49.22% | 41.07% | 45.74% | 46.03% | 46.1% | 38.38% | 28.7% | 16.21% | 14.38% | 15.44% | 0.1384
Solar Generated
Min | 0% | 226109330% | 226109330% | 0% | 0% | 444277812% | 444277812% | 605844335% | 6058443.35 | 8002798.36 | 8002798.36 | 8002798.36 | 8002798.36 | 8002798.36 | 4442778.12 | 6058443.35 | 6058443.35 | 8002798.36
Max | 0% | 226109330% | 226109330% | 0% | 0% | 444277812% | 4442778.12 | 605844335% | 6058443.35 | 8002798.36 | 8002798.36 | 8002798.36 | 8002798.36 | 8002798.36 | 4442778.12 | 6058443.35 | 6058443.35 | 8002798.36
Average | 0% | 226109330% | 2261093.3 | 0 | 0 | 4442778.12 | 4442778.12 | 6058443.35 | 6058443.35 | 8002798.36 | 8002798.36 | 8002798.36 | 8002798.36 | 8002798.36 | 4442778.12 | 6058443.35 | 6058443.35 | 8002798.36
Total | 0 | 2261093.3 | 2261093.3 | 0 | 0 | 4442778.12 | 4442778.12 | 6058443.35 | 6058443.35 | 8002798.36 | 8002798.36 | 8002798.36 | 8002798.36 | 8002798.36 | 4442778.12 | 6058443.35 | 6058443.35 | 8002798.36
Solar Spilled
Min | 0 | 0 | 0 | 0 | 0 | 79408.48 | 79408.48 | 724836.55 | 724836.55 | 3302668.13 | 3302668.13 | 3302668.13 | 3302668.13 | 3302668.13 | 79408.48 | 724836.55 | 724836.55 | 3302668.13
Max | 0 | 0 | 0 | 0 | 0 | 79408.48 | 79408.48 | 724836.55 | 724836.55 | 3302668.13 | 3302668.13 | 3302668.13 | 3302668.13 | 3302668.13 | 79408.48 | 724836.55 | 724836.55 | 3302668.13
Average | 0 | 0 | 0 | 0 | 0 | 79408.48 | 79408.48 | 724836.55 | 724836.55 | 3302668.13 | 3302668.13 | 3302668.13 | 3302668.13 | 3302668.13 | 79408.48 | 724836.55 | 724836.55 | 3302668.13
Total | 0 | 0 | 0 | 0 | 0 | 79408.48 | 79408.48 | 724836.55 | 724836.55 | 3302668.13 | 3302668.13 | 3302668.13 | 3302668.13 | 3302668.13 | 79408.48 | 724836.55 | 724836.55 | 3302668.13
Wind Generated
Min | 0 | 0 | 0 | 6906918.82 | 6834760.93 | 0 | 0 | 0 | 6393599.74 | 0 | 0 | 0 | 5869562.62 | 11281664.59 | 23450019.6 | 23008661.08 | 22316430.36 | 21430944.05
Max | 0 | 0 | 0 | 6906918.82 | 6834760.93 | 0 | 0 | 0 | 6393599.74 | 0 | 0 | 0 | 5869562.62 | 11281664.59 | 23450019.6 | 23008661.08 | 22316430.36 | 21430944.05
Average | 0 | 0 | 0 | 6906918.82 | 6834760.93 | 0 | 0 | 0 | 6393599.74 | 0 | 0 | 0 | 5869562.62 | 11281664.59 | 23450019.6 | 23008661.08 | 22316430.36 | 21430944.05
Total | 0 | 0 | 0 | 6906918.82 | 6834760.93 | 0 | 0 | 0 | 6393599.74 | 0 | 0 | 0 | 5869562.62 | 11281664.59 | 23450019.6 | 23008661.08 | 22316430.36 | 21430944.05
Wind Spilled
Min | 0 | 0 | 0 | 565.01 | 590.51 | 0 | 0 | 0 | 588751.54 | 0 | 0 | 0 | 1026385.72 | 2289572.94 | 10321951.9 | 11921188.91 | 11537083.14 | 13349070.95
Max | 0 | 0 | 0 | 565.01 | 590.51 | 0 | 0 | 0 | 588751.54 | 0 | 0 | 0 | 1026385.72 | 2289572.94 | 10321951.9 | 11921188.91 | 11537083.14 | 13349070.95
Average | 0 | 0 | 0 | 565.01 | 590.51 | 0 | 0 | 0 | 588751.54 | 0 | 0 | 0 | 1026385.72 | 2289572.94 | 10321951.9 | 11921188.91 | 11537083.14 | 13349070.95
Total | 0 | 0 | 0 | 565.01 | 590.51 | 0 | 0 | 0 | 588751.54 | 0 | 0 | 0 | 1026385.72 | 2289572.94 | 10321951.9 | 11921188.91 | 11537083.14 | 13349070.95
Weight
Fixed Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Volume
Fixed Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Min | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57
Average | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51 | 179.51
Max | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52 | 359.52
Tier (Only)
Load Service
Priority
Overall
Overall Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Total Load Served | 3931191113% | 3931189487% | 3931190040% | 3931188645% | 3931190174% | 3931189559% | 3931190757% | 3931190642% | 3931189119% | 3931191202% | 3931191060% | 39311920.08 | 39311903.27 | 39311905.24 | 39311921.59 | 39311925.43 | 39311926.17 | 39311923.42
Total Load Not Served | 2765% | 4391% | 3838% | 5234% | 3704% | 4320% | 3121% | 3236% | 47.59 | 26.76 | 28.18 | 18.7 | 35.51 | 33.55 | 17.19 | 13.35 | 12.61 | 15.36
Post-Startup
Post-Startup Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
DBT Occurrences w/ Post-Startup Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Total Post-Startup Load Served | 3931191113% | 3931189487% | 3931189711% | 3931188348% | 3931189835% | 3931189559% | 3931190428% | 3931190642% | 3931188822% | 3931191202% | 3931190732% | 39311916.45 | 39311900.3 | 39311902.1 | 39311918.13 | 39311921.96 | 39311922.36 | 39311919.95
Total Post-Startup Load Not Served | 2700% | 4325% | 3710% | 5074% | 3586% | 4254% | 2993% | 3171% | 45.99 | 26.11 | 26.89 | 17.76 | 33.91 | 32.11 | 16.08 | 12.25 | 11.85 | 14.26
Startup Time
Min | 17% | 17% | 1.17 | 1.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Max | 0.17 | 0.17 | 1.17 | 1.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Average | 0.17 | 0.17 | 1.17 | 1.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Renewable Penetration
Min | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
Max | 0% | 92.64% | 92.64% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Average | 0% | 7.95% | 7.95% | 18.67% | 18.52% | 15.52% | 15.52% | 20.79% | 37.35% | 26.82% | 26.82% | 26.82% | 41.67% | 54.99% | 74.46% | 77.7% | 75.94% | 0.7886
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= 0.00% | 0% | 50.9% | 50.9% | 7.39% | 8.34% | 50.9% | 50.9% | 50.9% | 3.52% | 50.9% | 50.9% | 50.9% | 4.64% | 4.43% | 5.07% | 3.81% | 5.1% | 0.0424
<= 25.00% | 0% | 36.4% | 36.4% | 61.54% | 60.74% | 26.99% | 26.99% | 21.92% | 41.92% | 16.69% | 16.69% | 16.69% | 38.58% | 17.73% | 11.76% | 10.3% | 10.84% | 0.0958
<= 50.00% | 0% | 10.16% | 10.16% | 30.07% | 29.89% | 9.41% | 9.41% | 8.69% | 28.63% | 7.73% | 7.73% | 7.73% | 25.24% | 25.26% | 7.64% | 6.95% | 7.02% | 0.0611
<= 75.00% | 0% | 2.47% | 2.47% | 0.97% | 1% | 6.34% | 6.34% | 5.8% | 8.56% | 4.78% | 4.78% | 4.78% | 7.82% | 20.33% | 9.74% | 9.25% | 9.14% | 0.0844
<= 100.00% | 0% | 0.07% | 0.07% | 0.03% | 0.03% | 6.35% | 6.35% | 12.69% | 17.37% | 19.9% | 19.9% | 19.9% | 23.73% | 32.25% | 65.79% | 69.69% | 67.9% | 0.7162
<= 110.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= 120.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= 130.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= 140.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
Diesel Fuel Use
Min | 292333004% | 278363629% | 278281366% | 246739905% | 247251928% | 262852953% | 262707728% | 250505583% | 2071840.37 | 2354984.3 | 2353821.54 | 2353197.05 | 1956358.93 | 1609589.98 | 910594.37 | 820564.25 | 870992.6 | 788321.14
Max | 292333004% | 278363629% | 278281366% | 246739905% | 247251928% | 262852953% | 2627077.28 | 250505583% | 2071840.37 | 2354984.3 | 2353821.54 | 2353197.05 | 1956358.93 | 1609589.98 | 910594.37 | 820564.25 | 870992.6 | 788321.14
Average | 292333004% | 278363629% | 2782813.66 | 2467399.05 | 2472519.28 | 2628529.53 | 2627077.28 | 2505055.83 | 2071840.37 | 2354984.3 | 2353821.54 | 2353197.05 | 1956358.93 | 1609589.98 | 910594.37 | 820564.25 | 870992.6 | 788321.14
Natural Gas Use
Min | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Max | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Average | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Spinning Reserve
Min | 6.25% | 6.25% | 4.93% | 6.73% | 6.73% | 0% | 6.25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
Max | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Average | 40.29% | 43.66% | 43.56% | 47.77% | 47.68% | 48.04% | 47.86% | 51.05% | 59.61% | 54.79% | 54.69% | 54.61% | 62.29% | 71.94% | 84.32% | 86.25% | 85.13% | 0.8689
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= 0.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.01% | 0.01% | 0.02% | 0.01% | 0.01% | 0.01% | 0.03% | 0.02% | 0.05% | 0.06% | 0.0009
<= 5.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= 10.00% | 0.05% | 0.06% | 0.05% | 0.01% | 0.01% | 0.06% | 0.05% | 0.05% | 0.01% | 0.04% | 0.04% | 0.04% | 0.01% | 0.01% | 0.01% | 0% | 0.01% | 0.0001
<= 15.00% | 0.36% | 0.37% | 0.37% | 0.14% | 0.15% | 0.34% | 0.34% | 0.34% | 0.12% | 0.32% | 0.31% | 0.31% | 0.11% | 0.06% | 0.04% | 0.03% | 0.04% | 0.0004
<= 20.00% | 2.63% | 2.81% | 2.8% | 1.15% | 1.19% | 2.58% | 2.57% | 2.44% | 0.8% | 2.23% | 2.19% | 2.2% | 0.77% | 0.36% | 0.3% | 0.22% | 0.27% | 0.0024
<= 25.00% | 6.16% | 5.9% | 5.88% | 2.74% | 2.85% | 5.37% | 5.42% | 5.1% | 2.12% | 4.76% | 4.8% | 4.82% | 2% | 1.06% | 0.76% | 0.62% | 0.74% | 0.0061
<= 30.00% | 10.33% | 9.48% | 9.51% | 4.96% | 5.1% | 8.54% | 8.68% | 8.09% | 3.79% | 7.44% | 7.57% | 7.58% | 3.68% | 1.96% | 1.64% | 1.43% | 1.65% | 0.0138
<= 40.00% | 27.03% | 23.18% | 23.48% | 16.61% | 16.67% | 21.64% | 22.03% | 20.48% | 11.63% | 19.39% | 19.61% | 19.78% | 11.48% | 5.61% | 4.36% | 3.65% | 4.29% | 0.0361
<= 50.00% | 33.37% | 26.37% | 26.48% | 29.52% | 29.41% | 23.99% | 23.94% | 23.08% | 18.95% | 21.37% | 21.4% | 21.49% | 17.94% | 8.35% | 5.6% | 4.69% | 5.2% | 0.047
<= 75.00% | 20.05% | 29.35% | 29.03% | 43.71% | 43.44% | 25.75% | 25.34% | 23.12% | 39.14% | 20.85% | 20.51% | 20.25% | 35% | 38.4% | 14.2% | 12.84% | 13.16% | 0.1171
<= 100.00% | 0.02% | 2.48% | 2.39% | 1.16% | 1.18% | 11.74% | 11.63% | 17.28% | 23.42% | 23.58% | 23.55% | 23.5% | 28.99% | 44.17% | 73.07% | 76.47% | 74.58% | 0.7762
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
Diesel Gen Set Data
JD 6619 Run Time (hours/year) | 3235.3176 | 3719.654 | 3755.2528 | 3633.53 | 3684.636 | 3610.1212 | 3649.8216 | 3681.3608 | 3067.6124 | 3504.3188 | 3516.3516 | 3555.8596 | 3004.1352 | 3088.6512 | 3285.0348 | 3251.6248 | 3256.2808 | 3262.9692
CAT 3406 Run Time (hours/year) | 6904.682 | 6252.5212 | 6491.1616 | 6361.012 | 6504.628 | 6480.3488 | 6258.316 | 6187.534 | 6606.324 | 6315.49 | 6295.446 | 6350.0212 | 6359.0772 | 5426.3012 | 5250.9168 | 5345.3744 | 5363.8904 | 5308.3232
SD 60 Run Time (hours/year) | 842.3532 | 288.9792 | 281.9012 | 295.0596 | 230.2512 | 481.0232 | 448.8428 | 380.1244 | 367.0776 | 397.3016 | 538.8956 | 479.2088 | 449.1144 | 1078.4204 | 1010.2776 | 978.1348 | 1043.8996 | 1045.1712
CMS K19G2 Run Time (hours/year) | 6.004 | 0.5076 | 16.0752 | 4.658 | 0.0088 | 3.6152 | 7.0548 | 9.6196 | 3.1752 | 0.01 | 9.9764 | 0.01 | 3.4304 | 20.2316 | 31.0236 | 12.8052 | 39.6168 | 14.7896
Total Run Time | 10988.3568 | 10261.662 | 10544.3908 | 10294.2596 | 10419.524 | 10575.1084 | 10364.0352 | 10258.6388 | 10044.1892 | 10217.1204 | 10360.6696 | 10385.0996 | 9815.7572 | 9613.6044 | 9577.2528 | 9587.9392 | 9703.6876 | 9631.2532
JD 6619 Run Time (hours) | 80882.94 | 92991.35 | 93881.32 | 90838.25 | 92115.9 | 90253.03 | 91245.54 | 92034.02 | 76690.31 | 87607.97 | 87908.79 | 88896.49 | 75103.38 | 77216.28 | 82125.87 | 81290.62 | 81407.02 | 81574.23
CAT 3406 Run Time (hours) | 172617.05 | 156313.03 | 162279.04 | 159025.3 | 162615.7 | 162008.72 | 156457.9 | 154688.35 | 165158.1 | 157887.25 | 157386.15 | 158750.53 | 158976.93 | 135657.53 | 131272.92 | 133634.36 | 134097.26 | 132708.08
SD 60 Run Time (hours) | 21058.83 | 7224.48 | 7047.53 | 7376.49 | 5756.28 | 12025.58 | 11221.07 | 9503.11 | 9176.94 | 9932.54 | 13472.39 | 11980.22 | 11227.86 | 26960.51 | 25256.94 | 24453.37 | 26097.49 | 26129.28
CMS K19G2 Run Time (hours) | 150.1 | 12.69 | 401.88 | 116.45 | 0.22 | 90.38 | 176.37 | 240.49 | 79.38 | 0.25 | 249.41 | 0.25 | 85.76 | 505.79 | 775.59 | 320.13 | 990.42 | 369.74
Total Run Time | 274708.92 | 256541.55 | 263609.77 | 257356.49 | 260488.1 | 264377.71 | 259100.88 | 256465.97 | 251104.73 | 255428.01 | 259016.74 | 259627.49 | 245393.93 | 240340.11 | 239431.32 | 239698.48 | 242592.19 | 240781.33
Assumptions
Horizon (years) | 25
Nominal Discount Rate | 3%
Load Inflation Rate | 1%
Fuel Cost Adjustment | 1
Heating fuel cost ($/gal) | 7.99
Diesel oil cost ($/gal) | 7.1633
HHV (Btu/gallon) | 134000
Conversion (kWh/Btu) | 0.00029307
Baseline total fuel use (gal/year) | 186075.5898
Baseline Gen O&M net present cost | -2655676.211
Baseline diesel fuel net present cost | -13815874.8773
Baseline heating fuel net present cost | -6752037.5899
Baseline total net present cost | 21141875662.7895
Energy Efficiency Cost Electrical Curve | 0.1493
Energy Efficiency Cost Electrical Curve | -0.9009
Energy Efficiency Cost Electrical Curve | 16.515
Energy Efficiency Cost Thermal Curve | 0.1123
Energy Efficiency Cost Thermal Curve | -0.6774
Energy Efficiency Cost Thermal Curve | 12.418
Baseline electrical load (kWh/year) | 1747196.0752
Baseline thermal load (kWh/year) | 2813162.6652
EE electrical load(kWh/year) | 1572476.4452
EE thermal load(kWh/year) | 1828555.7328
Assumed replacement usage (hours) | 80000
Gen replacement curve ($/kW) | 410.53
Gen replacement curve ($) | 105.26
202kW Gen O&M | 15.7808
314kW Gen O&M | 16.4528
365kW Gen O&M | 16.7588
397kW Gen O&M | 17.1422
Wind Replacement cost (First turbine) | 560000
Wind O&M Cost ($/kWh) | 17500
Solar O&M Cost ($/hour/100kW) | 0.54
EE electrical load reduction (%) | 0.1
EE thermal load reduction (%) | 0.35
EE electrical load reduction cost ($/kWh/year) | 0.22436
EE thermal load reduction cost ($/kWh/year) | 1.3964
EE electrical load reduction cost ($/kWh/year) | -39200.1016
EE thermal load reduction cost ($/kWh/year) | -1374919.8883 | -1414119.9899
Financial calculations
RE Purchase Cost | 0 | -550000 | -635000 | -950000 | -1035000 | -1050000 | -1135000 | -1550000 | -2500000 | -2550000 | -2635000 | -2670000 | -3500000 | -4200000 | -4800000 | -5300000 | -5385000 | -6300000
Stove Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kW of Stoves | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
# of Stoves | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gen Replacement Cost (per year)
JD 6619 | -3357.9491 | -3860.6438 | -3897.5919 | -3771.2553 | -3824.2984 | -3746.9592 | -3788.1644 | -3820.8991 | -3183.8872 | -3637.1465 | -3649.6354 | -3690.6409 | -3118.0039 | -3205.7234 | -3409.5508 | -3374.8744 | -3379.7069 | -3386.6488
CAT 3406 | -11134.8078 | -10083.1033 | -10467.9458 | -10258.0606 | -10489.6623 | -10450.5086 | -10092.4483 | -9978.302 | -10653.662 | -10184.6497 | -10152.3258 | -10240.3363 | -10254.9404 | -8750.7029 | -8467.87 | -8620.1966 | -8650.0564 | -8560.4462
SD 60 | -1578.8722 | -541.6507 | -528.384 | -553.0476 | -431.5734 | -901.6101 | -841.2925 | -712.4895 | -688.0352 | -744.6858 | -1010.0838 | -898.2093 | -841.8016 | -2021.3468 | -1893.6228 | -1833.3756 | -1956.6425 | -1959.0259
CMS | -12.2396 | -1.0348 | -32.7704 | -9.4957 | -0.017939 | -7.3698 | -14.3817 | -19.6102 | -6.4729 | -0.020386 | -20.3376 | -0.020386 | -6.9931 | -41.2436 | -63.2438 | -26.1043 | -80.7617 | -30.1496
New Small (100kW) Gen (purchase) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Gen O&M Cost (per year)
JD 6619 | -51055.7382 | -58698.9299 | -59260.7056 | -57339.8285 | -58146.3196 | -56970.4201 | -57596.9222 | -58094.6344 | -48409.2244 | -55300.7789 | -55490.6655 | -56114.1314 | -47407.5066 | -48741.2324 | -51840.3129 | -51313.0781 | -51386.5532 | -51492.1012
CAT 3406 | -113601.0068 | -102871.1682 | -106797.459 | -104656.1402 | -107019.0183 | -106619.5587 | -102966.5086 | -101801.95 | -108692.1972 | -103907.1781 | -103577.3992 | -104475.3113 | -104624.3074 | -89277.5771 | -86392.0214 | -87946.1087 | -88250.7478 | -87336.5145
SD 60 | -14116.7867 | -4842.9302 | -4724.3117 | -4944.8301 | -3858.7223 | -8061.3476 | -7522.0443 | -6370.4098 | -6151.7617 | -6658.2782 | -9031.2166 | -8030.9405 | -7526.596 | -18072.9779 | -16930.9897 | -16392.3166 | -17494.4524 | -17515.7628
CMS | -102.922 | -8.7014 | -275.565 | -79.8486 | -0.15085 | -61.9726 | -120.9351 | -164.9015 | -54.4301 | -0.17142 | -171.0179 | -0.17142 | -58.8048 | -346.815 | -531.8141 | -219.5099 | -679.1209 | -253.5269
Deasil Fuel use (Gal/year) | 116946 | 111339.6 | 111339.6 | 98725.2 | 98900.4 | 105120 | 105120 | 100214.4 | 82869.6 | 94170 | 94170 | 94170 | 78226.8 | 64386 | 36441.6 | 32850 | 34864.8 | 31536
Heating Fuel use (Gal/year) | 33964.1523 | 34378.237 | 34378.2615 | 35456.9616 | 35429.836 | 34964.122 | 34964.0874 | 35453.0549 | 37014.9946 | 36064.8065 | 36064.706 | 36064.7289 | 37508.085 | 39031.7087 | 42035.0567 | 42396.8594 | 42183.5042 | 42541.5269
Total Fuel usage (Gal/year) | 150910.1523 | 145717.837 | 145717.8615 | 134182.1616 | 134330.236 | 140084.122 | 140084.0874 | 135667.4549 | 119884.5946 | 130234.8065 | 130234.706 | 130234.7289 | 115734.885 | 103417.7087 | 78476.6567 | 75246.8594 | 77048.3042 | 74077.5269
New Wind Turbines (#) | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2 | 5 | 5 | 5 | 5
New 100kW Solar Fields (#) | 0 | 1 | 1 | 0 | 0 | 2 | 2 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 2 | 3 | 3 | 5
Wind Replacement Cost (per replacement) | 0 | 0 | 0 | -560000 | -560000 | 0 | 0 | 0 | -560000 | 0 | 0 | 0 | -560000 | -1092000 | -2520000 | -2520000 | -2520000 | -2520000
Wind Replacement NPV (Turbines are replaced every 20 years: this means that the first replacement is out of the time horizon for this analysis and so the replacement cost is not used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Replacement NPV (converter only after 10 years) | 0 | -63211.8617 | -63211.8617 | 0 | 0 | -126423.7234 | -126423.7234 | -189635.5851 | -189635.5851 | -316059.3085 | -316059.3085 | -316059.3085 | -316059.3085 | -316059.3085 | -126423.7234 | -189635.5851 | -189635.5851 | -316059.3085
Wind O&M Cost per year ($/year) | 0 | -17500 | -17500 | 0 | 0 | -34562.5 | -34562.5 | -51187.5 | -51187.5 | -83125 | -83125 | -83125 | -83125 | -83125 | -34562.5 | -51187.5 | -51187.5 | -83125
Solar O&M Cost per year ($/year) | 0 | -4730.4 | -4730.4 | 0 | 0 | -9460.8 | -9460.8 | -14191.2 | -14191.2 | -23652 | -23652 | -23652 | -23652 | -23652 | -9460.8 | -14191.2 | -14191.2 | -23652
Gen + Wind + Solar O&M + Genorator Replacement Cost
Year
1 | -194960.3224 | -203138.5622 | -208215.1335 | -181612.5065 | -183769.7631 | -230843.0468 | -226965.9971 | -246341.8966 | -243218.3705 | -287209.909 | -289879.6818 | -290226.7614 | -280615.9537 | -277234.6192 | -213552.7255 | -235104.2642 | -237256.7417 | -277311.176
2 | -183768.8023 | -191477.5777 | -196262.7331 | -171187.2057 | -173220.6269 | -217591.7116 | -213937.2203 | -232200.864 | -229256.6411 | -270722.8853 | -273239.4022 | -273566.558 | -264507.45 | -261320.2179 | -201293.9254 | -221608.3176 | -223637.2341 | -261392.3801
3 | -178416.3129 | -185900.5609 | -190546.3428 | -166201.1706 | -168175.366 | -211254.0889 | -207706.0392 | -225437.732 | -222579.2632 | -262837.7527 | -265280.973 | -265598.6 | -256803.3495 | -253708.9494 | -195430.9956 | -215153.7064 | -217123.5283 | -253779.0098
4 | -173219.7213 | -180485.9814 | -184996.4493 | -161360.3598 | -163277.0543 | -205101.0572 | -201656.3487 | -218871.5845 | -216096.372 | -255182.2841 | -257554.3427 | -257862.7185 | -249323.6403 | -246319.3684 | -189738.8306 | -208887.0936 | -210799.542 | -246387.3882
5 | -168174.4867 | -175229.1082 | -179608.2032 | -156660.5435 | -158521.412 | -199127.24 | -195782.8628 | -212496.684 | -209802.3029 | -247749.7904 | -250052.7599 | -250352.1539 | -242061.7867 | -239145.0178 | -184212.4569 | -202803.0035 | -204659.7496 | -239211.0565
6 | -163276.2007 | -170125.3478 | -174376.8963 | -152097.615 | -153904.2835 | -193327.4175 | -190080.4493 | -206307.4602 | -203691.5563 | -240533.7771 | -242769.6698 | -243060.3436 | -235011.4434 | -232179.629 | -178847.0456 | -196896.1199 | -198698.786 | -232243.7441
7 | -158520.5832 | -165170.2405 | -169297.9576 | -147667.5874 | -149421.6344 | -187696.5218 | -184544.1256 | -200298.505 | -197758.7925 | -233527.939 | -235698.7086 | -235980.9161 | -228166.4499 | -225417.1155 | -173637.9083 | -191161.2815 | -192911.4427 | -225479.3632
8 | -153903.4788 | -160359.4568 | -164366.9491 | -143366.5897 | -145069.548 | -182229.6328 | -179169.054 | -194464.568 | -191998.8277 | -226726.1543 | -228833.6976 | -229107.6855 | -221520.8251 | -218851.5684 | -168580.4935 | -185593.4771 | -187292.6628 | -218912.0031
9 | -149420.8532 | -155688.793 | -159579.5623 | -139190.8638 | -140844.2214 | -176921.9736 | -173950.5378 | -188800.5514 | -186406.6288 | -220122.4799 | -222168.6385 | -222434.6461 | -215068.7623 | -212477.2509 | -163670.3821 | -180187.8419 | -181837.5367 | -212535.9254
10 | -145068.7895 | -151154.168 | -154931.6138 | -135136.761 | -136741.9625 | -171768.9064 | -168884.0173 | -183301.5063 | -180977.3095 | -213711.1456 | -215697.7073 | -215955.9671 | -208804.6236 | -206288.5931 | -158903.2836 | -174939.6523 | -176541.2978 | -206345.5586
11 | -140843.485 | -146751.6194 | -150419.0426 | -131200.7388 | -132759.1869 | -166765.9286 | -163965.0653 | -177962.6274 | -175706.1257 | -207486.5491 | -209415.2498 | -209665.9875 | -202722.9355 | -200280.1875 | -154275.0326 | -169844.3226 | -171399.3182 | -200335.4938
12 | -136741.2476 | -142477.3004 | -146037.9054 | -127379.358 | -128892.4144 | -161908.6685 | -159189.3838 | -172779.2499 | -170588.4716 | -201443.2515 | -203315.7765 | -203559.2112 | -196818.384 | -194446.784 | -149781.585 | -164897.4006 | -166407.1051 | -194500.4794
13 | -132758.4928 | -138327.4761 | -141784.3742 | -123669.2797 | -125138.2664 | -157192.882 | -154552.7998 | -167746.8446 | -165619.8753 | -195575.9724 | -197393.9577 | -197630.3021 | -191085.8097 | -188783.2854 | -145419.0146 | -160094.5637 | -161560.2962 | -188835.4169
14 | -128891.7406 | -134298.5205 | -137654.7322 | -120067.2618 | -121493.4626 | -152614.4486 | -150051.262 | -162861.0142 | -160795.9955 | -189879.5848 | -191644.6192 | -191874.0797 | -185520.2036 | -183284.7431 | -141183.5093 | -155431.6153 | -156854.6565 | -183335.3562
15 | -125137.6122 | -130386.9131 | -133645.3711 | -116570.1571 | -117954.818 | -148169.3676 | -145680.8369 | -158117.4895 | -156112.617 | -184349.1115 | -186062.737 | -186285.5143 | -180116.7025 | -177946.3525 | -137071.3683 | -150904.4808 | -152286.0743 | -177995.4915
16 | -121492.8274 | -126589.236 | -129752.7875 | -113174.9098 | -114519.2408 | -143853.7549 | -141437.7057 | -153512.1257 | -151565.6475 | -178979.7199 | -180643.434 | -180859.7226 | -174870.585 | -172763.4491 | -133078.9983 | -146509.2047 | -147850.5575 | -172811.1568
17 | -117954.2013 | -122902.1709 | -125973.5801 | -109878.5532 | -111183.7289 | -139663.8397 | -137318.1609 | -149040.8988 | -147151.1141 | -173766.7183 | -175381.9748 | -175591.9637 | -169777.267 | -167731.504 | -129202.911 | -142241.9463 | -143544.2306 | -167777.8221
18 | -114518.6421 | -119322.496 | -122304.4467 | -106678.207 | -107945.3679 | -135595.9609 | -133318.6028 | -144699.9017 | -142865.1593 | -168705.5518 | -170273.7619 | -170477.6346 | -164832.298 | -162846.1203 | -125439.7194 | -138098.977 | -139363.3307 | -162891.0894
19 | -111183.1476 | -115847.0835 | -118742.1812 | -103571.0748 | -104801.3281 | -131646.564 | -129435.5367 | -140485.3415 | -138704.0382 | -163791.7978 | -165314.332 | -165512.2666 | -160031.3573 | -158103.0295 | -121786.1353 | -134076.6767 | -135304.2046 | -158146.6888
20 | -107944.8035 | -112472.8966 | -115283.6711 | -100554.4415 | -101748.8622 | -127812.198 | -125665.5696 | -136393.5354 | -134664.1147 | -159021.163 | -160499.3514 | -160691.521 | -155370.2498 | -153498.0869 | -118238.9663 | -130171.5308 | -131363.3054 | -153540.4745
Total Gen O&M + Replacement Cost | -2906195.751 | -3028105.5092 | -3103779.933 | -2707225.1844 | -2739382.5483 | -3441085.2092 | -3383291.5756 | -3672120.3808 | -3625559.2235 | -4281323.5374 | -4321120.7755 | -4326294.5536 | -4183030.0767 | -4173784.1318 | -3224503.5472 | -3545763.7366 | -3577849.8608 | -4174925.3346
Diesel Fuel Cost
Year
1 | -837723.18 | -797562.668 | -797562.668 | -707201.516 | -708456.532 | -753009.6 | -753009.6 | -717869.152 | -593622.568 | -674571.1 | -674571.1 | -674571.1 | -560364.644 | -461218.38 | -261043.328 | -235315.5 | -249748.184 | -225902.88
2 | -789634.4425 | -751779.3081 | -751779.3081 | -666605.2559 | -667788.2289 | -709783.7685 | -709783.7685 | -676660.526 | -559546.2042 | -635847.9593 | -635847.9593 | -635847.9593 | -528197.4211 | -434742.5582 | -246058.3731 | -221807.4277 | -235411.6166 | -212935.1305
3 | -766635.381 | -729882.8234 | -729882.8234 | -647189.5688 | -648338.0863 | -689110.4549 | -689110.4549 | -656951.967 | -543248.7419 | -617328.1158 | -617328.1158 | -617328.1158 | -512813.0302 | -422080.1536 | -238891.6243 | -215347.0171 | -228554.9675 | -206733.1365
4 | -744306.1952 | -708624.1004 | -708624.1004 | -628339.3872 | -629454.4527 | -669039.2766 | -669039.2766 | -637817.4437 | -527425.963 | -599347.6852 | -599347.6852 | -599347.6852 | -497876.7283 | -409786.5569 | -231933.6159 | -209074.7739 | -221898.0267 | -200711.783
5 | -722627.374 | -687984.5635 | -687984.5635 | -610038.24 | -611120.8279 | -649552.6957 | -649552.6957 | -619240.2366 | -512064.0418 | -581890.9566 | -581890.9566 | -581890.9566 | -483375.4644 | -397851.0261 | -225178.2678 | -202985.2174 | -215434.9774 | -194865.8087
6 | -701579.9747 | -667946.1782 | -667946.1782 | -592270.136 | -593321.1921 | -630633.6851 | -630633.6851 | -601204.1132 | -497149.5551 | -564942.6763 | -564942.6763 | -564942.6763 | -469296.5674 | -386263.1321 | -218619.6775 | -197073.0266 | -209160.1722 | -189190.1055
7 | -681145.6065 | -648491.4351 | -648491.4351 | -575019.5495 | -576039.9923 | -612265.7137 | -612265.7137 | -583693.3137 | -482669.471 | -548488.0352 | -548488.0352 | -548488.0352 | -455627.7353 | -375012.7497 | -212252.1141 | -191333.0355 | -203068.1284 | -183679.7141
8 | -661306.4141 | -629603.3351 | -629603.3351 | -558271.4073 | -559262.1285 | -594432.7318 | -594432.7318 | -566692.5376 | -468611.1369 | -532512.6555 | -532512.6555 | -532512.6555 | -442357.0246 | -364090.0482 | -206070.0137 | -185760.2287 | -197153.5227 | -178329.8195
9 | -642045.0622 | -611265.3738 | -611265.3738 | -542011.075 | -542972.9403 | -577119.1571 | -577119.1571 | -550186.9297 | -454962.2688 | -517002.5782 | -517002.5782 | -517002.5782 | -429472.8394 | -353485.4837 | -200067.9744 | -180349.7366 | -191411.1871 | -173135.7471
10 | -623344.7206 | -593461.528 | -593461.528 | -526224.3447 | -527158.1944 | -560309.8612 | -560309.8612 | -534162.0677 | -441710.9406 | -501944.2507 | -501944.2507 | -501944.2507 | -416963.9217 | -343189.79 | -194240.7519 | -175096.8316 | -185836.104 | -168092.9584
11 | -605189.0491 | -576176.2408 | -576176.2408 | -510897.422 | -511804.0723 | -543990.1565 | -543990.1565 | -518603.9492 | -428845.5734 | -487324.5152 | -487324.5152 | -487324.5152 | -404819.3415 | -333193.9709 | -188583.2543 | -169996.9239 | -180423.4019 | -163197.047
12 | -587562.1836 | -559394.4085 | -559394.4085 | -496016.9146 | -496897.1575 | -528145.783 | -528145.783 | -503498.9798 | -416354.9256 | -473130.5973 | -473130.5973 | -473130.5973 | -393028.4869 | -323489.2921 | -183090.5381 | -165045.5572 | -175168.3514 | -158443.7349
13 | -570448.722 | -543101.3675 | -543101.3675 | -481569.82 | -482424.4248 | -512762.8961 | -512762.8961 | -488833.961 | -404228.0831 | -459350.0945 | -459350.0945 | -459350.0945 | -381581.0552 | -314067.2739 | -177757.804 | -160238.405 | -170066.3606 | -153828.8688
14 | -553833.7106 | -527282.8811 | -527282.8811 | -467543.5145 | -468373.228 | -497828.0545 | -497828.0545 | -474596.0786 | -392454.4496 | -445970.9655 | -445970.9655 | -445970.9655 | -370467.0439 | -304919.6834 | -172580.3922 | -155571.267 | -165112.9714 | -149348.4164
15 | -537702.6317 | -511925.1273 | -511925.1273 | -453925.7423 | -454731.2893 | -483328.2083 | -483328.2083 | -460772.8919 | -381023.7375 | -432981.5199 | -432981.5199 | -432981.5199 | -359676.7417 | -296038.5276 | -167553.7789 | -151040.0651 | -160303.8557 | -144998.4625
16 | -522041.39 | -497014.6867 | -497014.6867 | -440704.6041 | -441486.6886 | -469250.6876 | -469250.6876 | -447352.3222 | -369925.9588 | -420370.4077 | -420370.4077 | -420370.4077 | -349200.72 | -287416.0462 | -162673.5717 | -146640.8399 | -155634.8114 | -140775.2063
17 | -506836.301 | -482538.5307 | -482538.5307 | -427868.5477 | -428627.853 | -455583.1919 | -455583.1919 | -434322.6429 | -359151.4163 | -408126.6094 | -408126.6094 | -408126.6094 | -339029.8253 | -279044.705 | -157935.5065 | -142369.7475 | -151101.7586 | -136674.9576
18 | -492074.0786 | -468484.0104 | -468484.0104 | -415406.357 | -416143.5466 | -442313.7785 | -442313.7785 | -421672.4689 | -348690.6954 | -396239.4266 | -396239.4266 | -396239.4266 | -329155.1702 | -270917.1893 | -153335.4432 | -138223.0558 | -146700.7365 | -132694.1336
19 | -477741.8239 | -454838.8451 | -454838.8451 | -403307.1427 | -404022.8608 | -429430.8529 | -429430.8529 | -409390.7465 | -338534.6557 | -384698.4724 | -384698.4724 | -384698.4724 | -319568.1264 | -263026.3974 | -148869.3624 | -134197.1415 | -142427.8996 | -128829.2559
20 | -463827.0135 | -441591.1117 | -441591.1117 | -391560.3327 | -392255.2047 | -416923.1582 | -416923.1582 | -397466.7441 | -328674.423 | -373493.6625 | -373493.6625 | -373493.6625 | -310260.3169 | -255365.4344 | -144533.3615 | -130288.4869 | -138279.5141 | -125076.9475
Total Diesel Fuel Cost | -12487605.2547 | -11888948.5234 | -11888948.5234 | -10541970.878 | -10560678.9008 | -11224813.7121 | -11224813.7121 | -10700989.0722 | -8848894.8097 | -10055562.2838 | -10055562.2838 | -10055562.2838 | -8353132.2041 | -6875198.3987 | -3891268.7535 | -3507754.285 | -3722896.5479 | -3367444.1136
Heating Fuel Cost
Year
1 | -271373.5769 | -274682.1139 | -274682.309 | -283301.123 | -283084.3896 | -279363.335 | -279363.0584 | -283269.9089 | -295749.8066 | -288157.8043 | -288157.0011 | -288157.184 | -299689.5994 | -311863.3528 | -335860.1029 | -338750.9068 | -337046.1982 | -339906.8001
2 | -255795.6235 | -258914.2368 | -258914.4208 | -267038.4796 | -266834.1876 | -263326.7367 | -263326.4761 | -267009.0573 | -278772.5578 | -271616.3675 | -271615.6105 | -271615.7828 | -282486.1904 | -293961.1205 | -316580.3591 | -319305.219 | -317698.3676 | -320394.7592
3 | -248345.2655 | -251373.0455 | -251373.2241 | -259260.6598 | -259062.3181 | -255657.0259 | -255656.7729 | -259232.0945 | -270652.9687 | -263705.2112 | -263704.4762 | -263704.6435 | -274258.4373 | -285399.1462 | -307359.5719 | -310005.0669 | -308445.0171 | -311062.8731
4 | -241111.9082 | -244051.5005 | -244051.6739 | -251709.3785 | -251516.8136 | -248210.7048 | -248210.4591 | -251681.6451 | -262769.8726 | -256024.4769 | -256023.7633 | -256023.9258 | -266270.3275 | -277086.5497 | -298407.3514 | -300975.7932 | -299461.1816 | -302002.7894
5 | -234089.2313 | -236943.2043 | -236943.3727 | -244378.0374 | -244191.0812 | -240981.2668 | -240981.0282 | -244351.1118 | -255116.3811 | -248567.4533 | -248566.7605 | -248566.9182 | -258514.881 | -269016.0676 | -289715.8751 | -292209.5079 | -290739.0113 | -293206.5916
6 | -227271.0984 | -230041.946 | -230042.1094 | -237260.2305 | -237078.7196 | -233962.3949 | -233962.1633 | -237234.0891 | -247685.8069 | -241327.6245 | -241326.9519 | -241327.1051 | -250985.3214 | -261180.6482 | -281277.5487 | -283698.5514 | -282270.8848 | -284666.5938
7 | -220651.5518 | -223341.6951 | -223341.8538 | -230349.7383 | -230173.5142 | -227147.9563 | -227147.7314 | -230324.3584 | -240471.6572 | -234298.6646 | -234298.0116 | -234298.1603 | -243675.0693 | -253573.4448 | -273084.9987 | -275435.4868 | -274049.4027 | -276375.3338
8 | -214224.8076 | -216836.5972 | -216836.7512 | -223640.5226 | -223469.4313 | -220531.9964 | -220531.7781 | -223615.8819 | -233467.6283 | -227474.4317 | -227473.7976 | -227473.942 | -236577.7372 | -246187.8105 | -265131.0667 | -267413.094 | -266067.3812 | -268325.5668
9 | -207985.2501 | -210520.9681 | -210521.1177 | -217126.721 | -216960.6129 | -214108.7343 | -214108.5224 | -217102.798 | -226667.6003 | -220848.9628 | -220848.3472 | -220848.4874 | -229687.1235 | -239017.2918 | -257408.8026 | -259624.3631 | -258317.8459 | -260510.259
10 | -201927.4273 | -204389.2895 | -204389.4347 | -210802.6417 | -210641.3717 | -207872.5576 | -207872.3518 | -210779.4155 | -220065.6314 | -214416.4687 | -214415.8711 | -214416.0072 | -222997.2073 | -232055.6231 | -249911.4589 | -252062.4884 | -250794.0251 | -252922.5816
11 | -196046.0459 | -198436.2034 | -198436.3443 | -204662.759 | -204506.1861 | -201818.0171 | -201817.8173 | -204640.2092 | -213655.9528 | -208171.3288 | -208170.7486 | -208170.8807 | -216502.143 | -225296.7214 | -242632.4843 | -244720.8625 | -243489.3448 | -245555.9044
12 | -190335.9669 | -192656.5081 | -192656.645 | -198701.7077 | -198549.6953 | -195939.8224 | -195939.6285 | -198679.8148 | -207432.9639 | -202108.0863 | -202107.5229 | -202107.6512 | -210196.2553 | -218734.681 | -235565.5188 | -237593.0704 | -236397.4221 | -238403.7907
13 | -184792.2008 | -187045.1535 | -187045.2864 | -192914.2794 | -192766.6944 | -190232.8373 | -190232.649 | -192893.0241 | -201391.2271 | -196221.443 | -196220.8961 | -196221.0206 | -204074.0343 | -212363.768 | -228704.3871 | -230672.8839 | -229512.0603 | -231459.991
14 | -179409.9037 | -181597.2364 | -181597.3654 | -187295.4169 | -187152.1305 | -184692.075 | -184691.8922 | -187274.7806 | -195525.4632 | -190506.2553 | -190505.7243 | -190505.8452 | -198130.1304 | -206178.4155 | -222043.0943 | -223954.2562 | -222827.243 | -224718.4379
15 | -174184.3726 | -176307.9965 | -176308.1218 | -181840.2105 | -181701.0976 | -179312.6942 | -179312.5167 | -181820.1754 | -189830.5468 | -184957.5294 | -184957.0139 | -184957.1313 | -192359.3499 | -200173.2189 | -215575.8197 | -217431.3167 | -216337.1291 | -218173.2406
16 | -169111.0413 | -171172.8122 | -171172.9338 | -176543.8937 | -176408.8326 | -174089.9944 | -174089.8221 | -176524.4421 | -184301.5017 | -179570.4169 | -179569.9164 | -179570.0304 | -186756.6504 | -194342.931 | -209296.9124 | -211098.3657 | -210036.0477 | -211818.6802
17 | -164185.477 | -166187.1963 | -166187.3143 | -171401.8386 | -171270.7113 | -169019.412 | -169019.2447 | -171382.9535 | -178933.4968 | -174340.2106 | -174339.7247 | -174339.8353 | -181317.1363 | -188682.4573 | -203200.8858 | -204949.8697 | -203918.4929 | -205649.2041
18 | -159403.3757 | -161346.7925 | -161346.9071 | -166409.552 | -166282.244 | -164096.5165 | -164096.3541 | -166391.217 | -173721.8416 | -169262.3404 | -169261.8686 | -169261.976 | -176036.0546 | -183186.8517 | -197282.4134 | -198980.456 | -197979.1193 | -199659.4215
19 | -154760.559 | -156647.3714 | -156647.4826 | -161562.6719 | -161439.0718 | -159317.0063 | -159316.8486 | -161544.8709 | -168661.9821 | -164332.3693 | -164331.9113 | -164332.0156 | -170908.7909 | -177851.3124 | -191536.3237 | -193184.9087 | -192212.7372 | -193844.0985
20 | -150252.9699 | -152084.8266 | -152084.9346 | -156856.963 | -156736.9629 | -154676.7052 | -154676.5521 | -156839.6805 | -163749.4972 | -159545.9896 | -159545.5449 | -159545.6462 | -165930.865 | -172671.1771 | -185957.5958 | -187558.1638 | -186614.308 | -188198.1539
Total Heating Fuel Cost | -4045257.6533 | -4094576.6936 | -4094579.6027 | -4223056.8251 | -4219826.0664 | -4164357.7893 | -4164353.667 | -4222591.5286 | -4408624.3841 | -4295453.4352 | -4295441.4628 | -4295444.1887 | -4467353.3042 | -4648822.5896 | -5006532.5711 | -5049624.631 | -5024213.2201 | -5066855.0712
Total Net Present Cost | -20853178.649 | -21038962.5778 | -21199639.9108 | -19836372.8774 | -19969007.5055 | -21420800.4239 | -21448002.6681 | -21749456.5567 | -20986833.9924 | -22912518.5548 | -23037303.8205 | -23077480.3245 | -22233694.8835 | -21627984.4185 | -18462848.5852 | -19006898.2276 | -19313715.2038 | -20639403.8179
Marginal Net Present Value (NPC-Baseline) | -21162728841.4385 | -21162914625.3673 | -21163075302.7002 | -21161712035.6669 | -21161844670.2949 | -21163296463.2134 | -21163323665.4575 | -21163625119.3461 | -21162862496.7818 | -21164788181.3443 | -21164912966.61 | -21164953143.1139 | -21164109357.673 | -21163503647.208 | -21160338511.3747 | -21160882561.0171 | -21161189377.9932 | -21162515066.6074
Net Reduction in Imported Fuel | 18.9% | 21.69% | 21.69% | 27.89% | 27.81% | 24.72% | 24.72% | 27.09% | 35.57% | 30.01% | 30.01% | 30.01% | 37.8% | 44.42% | 57.83% | 59.56% | 58.59% | 60.19%
Marginal NPV = NPC - NPC(baseline) - capital investment | Highest NPV Cases
Marginal NPV (Utility Only) | 1077750.0826 | 941285.194 | 780610.7702 | 2272355.0259 | 2136489.6392 | 629228.4436 | 602022.0772 | 358806.0503 | 1307461.47 | -731394.0414 | -856191.2795 | -896365.0575 | 119329.499 | 906509.2494 | 4429355.0642 | 3928397.4817 | 3596169.0946 | 2313122.3316
Marginal NPV (Heating Customers Only) | 1331860.0482 | 1282541.008 | 1282538.0989 | 1154060.8765 | 1157291.6352 | 1212759.9123 | 1212764.0345 | 1154526.1729 | 968493.3174 | 1081664.2664 | 1081676.2388 | 1081673.5129 | 909764.3973 | 728295.112 | 370585.1304 | 327493.0705 | 352904.4815 | 310262.6303
Total Marginal NPV | 2409610.1308 | 2223826.202 | 2063148.8691 | 3426415.9024 | 3293781.2744 | 1841988.3559 | 1814786.1118 | 1513332.2232 | 2275954.7875 | 350270.225 | 225484.9593 | 185308.4554 | 1029093.8963 | 1634804.3613 | 4799940.1946 | 4255890.5522 | 3949073.5761 | 2623384.9619
Total % ROI | 270.4% | 213.2% | 200.7% | 244.9% | 234.5% | 174.8% | 171.2% | 151.1% | 158.1% | 108.8% | 105.6% | 104.5% | 120.9% | 129.1% | 177.2% | 163.4% | 158.1% | 134%
Normalized to Energy Efficient System
Normalized NPV (Utility Only) |  | -136464.8886 | -297139.3124 | 1194604.9433 | 1058739.5566 | -448521.639 | -475728.0054 | -718944.0323 | 229711.3874 | -1809144.124 | -1933941.3621 | -1974115.1401 | -958420.5836 | -171240.8332 | 3351604.9816 | 2850647.3991 | 2518419.012 | 1235372.249
Normalized NPV (Heating Customers Only) |  | -49319.0403 | -49321.9494 | -177799.1718 | -174568.4131 | -119100.1359 | -119096.0137 | -177333.8753 | -363366.7308 | -250195.7819 | -250183.8095 | -250186.5354 | -422095.6509 | -603564.9363 | -961274.9178 | -1004366.9777 | -978955.5668 | -1021597.4179
Normalized Total NPV |  | -185783.9288 | -346461.2618 | 1016805.7715 | 884171.1435 | -567621.775 | -594824.0191 | -896277.9077 | -133655.3434 | -2059339.9059 | -2184125.1715 | -2224301.6755 | -1380516.2345 | -774805.7695 | 2390330.0638 | 1846280.4213 | 1539463.4452 | 213774.831
Normalized % ROI |  | 66.22% | 45.44% | 207% | 185.4% | 45.94% | 47.59% | 42.18% | 94.65% | 19.24% | 17.11% | 16.69% | 60.56% | 81.55% | 149.8% | 134.8% | 128.6% | 103.4%
No Generator
100kW Diesel
Note on A225: Author: Already Included in Purchase Cost
Note on A234: Author: If the generator utilization is less than 30% then a new small generator is purchased (This assumes that the O&M costs for the generator set would not change as the O&M cost for the new generator would offset some of the O&M cost for the existing generator)
Note on B334: Author: NPV Values are normalized to the Baseline
Note on C334: Author: NPV Values are normalized to the Baseline
Note on D334: Author: NPV Values are normalized to the Baseline
Note on E334: Author: NPV Values are normalized to the Baseline
Note on F334: Author: NPV Values are normalized to the Baseline
Note on G334: Author: NPV Values are normalized to the Baseline
Note on H334: Author: NPV Values are normalized to the Baseline
Note on I334: Author: NPV Values are normalized to the Baseline
Note on J334: Author: NPV Values are normalized to the Baseline
Note on K334: Author: NPV Values are normalized to the Baseline
Note on L334: Author: NPV Values are normalized to the Baseline
Note on M334: Author: NPV Values are normalized to the Baseline
Note on N334: Author: NPV Values are normalized to the Baseline
Note on O334: Author: NPV Values are normalized to the Baseline
Note on P334: Author: NPV Values are normalized to the Baseline
Note on Q334: Author: NPV Values are normalized to the Baseline
Note on R334: Author: NPV Values are normalized to the Baseline
Note on S334: Author: NPV Values are normalized to the Baseline
Note on A335: Author: Value of Heating Fuel Deferred - Cost of Stove System
Note on B335: Author: NPV Values are normalized to the Baseline
Note on A341: Author: Value of Heating Fuel Deferred - Cost of Stove System

## High-EE Detailed
Summary Results
New Solar | No Generator | No Generator | SG 200 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 100 | SG 200 | SG 200 | SG 300 | SG 500 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | WG 100 | WG 100 | WG 500 | WG 500 | WG 500 | WG 500 | WG 500 | WG 500
New Storage | No Battery | Bat 100/100 | No Battery | No Battery | No Battery | No Battery | Bat 100/100 | No Battery | Bat 100/100 | No Battery | No Battery | Bat 50/50 | No Battery | No Battery | Bat 100/100
New Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel
Energy Efficiency Cost | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839
Renewable Energy Purchase Cost | 0 | -120000 | -1050000 | -1550000 | -2500000 | -2550000 | -2670000 | -3500000 | -3620000 | -4300000 | -4800000 | -4885000 | -5300000 | -6300000 | -6420000
Stove Purchase Cost | 0 | 0 | -10264.69 | -11931.14 | -13397.23 | -18115.3 | -18115.3 | -20582.77 | -20583.65 | -33002.13 | -36791.6 | -36730.59 | -41346.51 | -50314.81 | -50234.31
New Generator Purchase Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Net Reduction in Imported Fuel | 25.74% | 25.74% | 31.69% | 34.39% | 42.87% | 38.6% | 38.65% | 46.9% | 46.89% | 68.68% | 70.59% | 70.38% | 72.54% | 75.38% | 75.03%
Marginal NPV (Utility Only) | 1854284.5272 | 1733673.1149 | 1473672.9088 | 1122096.0587 | 2131643.1934 | 64.1842 | -125052.1368 | 857711.127 | 753506.792 | 5718748.8035 | 5067367.2644 | 4941818.8673 | 4373930.432 | 2770880.2229 | 2581060.944
Marginal NPV (Heating Customers Only) | 532501.4534 | 532499.1927 | 421058.2554 | 454601.1325 | 351415.6822 | 714473.2948 | 714473.2948 | 672244.2313 | 671568.0331 | 835282.5497 | 1003656.3486 | 1009713.1623 | 1221895.8297 | 1676131.3916 | 1681551.4337
Total Marginal NPV | 2386785.9806 | 2266172.3076 | 1894731.1642 | 1576697.1912 | 2483058.8756 | 714537.479 | 589421.158 | 1529955.3583 | 1425074.8251 | 6554031.3532 | 6071023.613 | 5951532.0296 | 5595826.2617 | 4447011.6145 | 4262612.3777
Total % ROI | 178.5% | 171.7% | 146.2% | 134.3% | 144.7% | 112.7% | 110.3% | 123.3% | 121.3% | 188.9% | 177.1% | 174.7% | 166.8% | 147.4% | 144.8%
Total Capital Cost | 3040717.2839 | 3160717.2839 | 4100981.9739 | 4602648.4239 | 5554114.5139 | 5608832.5839 | 5728832.5839 | 6561300.0539 | 6681300.9339 | 7414877.6739 | 7918667.1439 | 8003606.1339 | 8423222.0539 | 9432190.3539 | 9552109.8539
Raw DATA
Simulation Statistics | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Total Sim Time | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Power Utility Statistics
Failure Statistics
Occurrences | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations")
Downtime
Min | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Max | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Average | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Total | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Thermal Load Service
Overall
Overall Energy Availability | 29.67% | 29.67% | 27.24% | 26.09% | 22.3% | 24.68% | 24.68% | 21.05% | 21.03% | 10.67% | 9.995% | 10.19% | 9.516% | 9.088% | 9.292%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Total Load Served | 11474756 | 11474729 | 10536924 | 10093031 | 8624605 | 9545591 | 9545592 | 8141852 | 8135980 | 4127441 | 3866175 | 3941593 | 3680924 | 3515495 | 3594124
Total Load Not Served | 2720623000% | 2720625600% | 28144061 | 28587955 | 30056381 | 29135395 | 29135394 | 30539134 | 30545006 | 34553545 | 34814811 | 34739392 | 35000061 | 35165491 | 35086861
Post-Startup
Post-Startup Energy Availability
DBT Occurrences w/ Post-Startup Load Loss
Total Post-Startup Load Served | 11474756 | 11474729 | 10536924 | 10093031 | 8624605 | 9545591 | 9545592 | 8141852 | 8135980 | 4127441 | 3866175 | 3941593 | 3680924 | 3515495 | 3594124
Total Post-Startup Load Not Served | 27206230 | 27206256 | 28144061 | 28587955 | 30056381 | 29135395 | 29135394 | 30539134 | 30545006 | 34553545 | 34814811 | 34739392 | 35000061 | 35165491 | 35086861
Variable Selections
New Solar | No Generator | No Generator | SG 200 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 100 | SG 200 | SG 200 | SG 300 | SG 500 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | WG 100 | WG 100 | WG 500 | WG 500 | WG 500 | WG 500 | WG 500 | WG 500
New Storage | No Battery | Bat 100/100 | No Battery | No Battery | No Battery | No Battery | Bat 100/100 | No Battery | Bat 100/100 | No Battery | No Battery | Bat 50/50 | No Battery | No Battery | Bat 100/100
Metric Values
Purchase Cost | 0 | 120000 | 1060264.69 | 1561931.14 | 2513397.23 | 2568115.3 | 2688115.3 | 3520582.77 | 3640583.65 | 4333002.13 | 4836791.6 | 4921730.59 | 5341346.51 | 6350314.81 | 6470234.31
Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Diesel Fuel Used (Gal/Hour) | 12.63 | 12.63 | 11.27 | 10.73 | 8.83 | 10.09 | 10.08 | 8.29 | 8.29 | 3.83 | 3.59 | 3.64 | 3.39 | 3.23 | 3.31
Heating Fuel Deferred (GHFE/Year) | 11860.2 | 11860.18 | 11010.7 | 11306.32 | 10452.28 | 13540.14 | 13540.14 | 13206.3 | 13200.63 | 14679.45 | 16124.94 | 16175.28 | 17995.53 | 21884.61 | 21929.44
Average Renewable Energy Spilled | 0 | 0 | 115935.97 | 845840.65 | 1487986.36 | 3554503.35 | 3554503.35 | 4635251.27 | 4635639.6 | 10074934.58 | 11734718.77 | 11708000.39 | 13729770.06 | 17657887.29 | 17622629.96
Diesel Utilization | 58.55% | 58.58% | 51.28% | 48.49% | 39.19% | 45.11% | 45.19% | 36.38% | 36.48% | 15.38% | 14.25% | 14.51% | 13.33% | 12.66% | 13.02%
Heating Fuel Deferred from Waste Heat (GHFE/Year) | 11687.6126 | 11687.5851 | 10732.3838 | 10280.2566 | 8784.5913 | 9722.6616 | 9722.6626 | 8292.8832 | 8286.9023 | 4204.005 | 3937.8925 | 4014.7095 | 3749.2051 | 3580.7074 | 3660.7949
Heating Fuel Deferred from Stoves (GHFE/Year) | 172.5874 | 172.5949 | 278.3162 | 1026.0634 | 1667.6887 | 3817.4784 | 3817.4774 | 4913.4168 | 4913.7277 | 10475.445 | 12187.0475 | 12160.5705 | 14246.3249 | 18303.9026 | 18268.6451
Cost
Fixed Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Cost | 0 | 120000 | 1050000 | 1550000 | 2500000 | 2550000 | 2670000 | 3500000 | 3620000 | 4300000 | 4800000 | 4885000 | 5300000 | 6300000 | 6420000
Total Cost | 0 | 120000 | 1050000 | 1550000 | 2500000 | 2550000 | 2670000 | 3500000 | 3620000 | 4300000 | 4800000 | 4885000 | 5300000 | 6300000 | 6420000
Generation
Total Diesel Generation | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278
Total Solar Generation | 0 | 0 | 200 | 300 | 300 | 500 | 500 | 500 | 500 | 100 | 200 | 200 | 300 | 500 | 500
Total Wind Generation | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 500 | 500 | 500 | 500 | 500 | 500
Overall Diesel Efficiency | 34.92% | 34.93% | 31.9% | 30.07% | 27.32% | 27.85% | 27.88% | 25.31% | 25.35% | 11.49% | 10.68% | 10.8% | 9.97% | 9.4% | 0.0959
Overall Diesel Utilization | 58.55% | 58.58% | 51.28% | 48.49% | 39.19% | 45.11% | 45.19% | 36.38% | 36.48% | 15.38% | 14.25% | 14.51% | 13.33% | 12.66% | 0.1302
Solar Generated
Min | 0 | 0 | 4406250.63 | 5937439.25 | 5937439.25 | 7750963.15 | 7750963.15 | 7750963.15 | 7750963.15 | 2261093.3 | 4406250.63 | 4406250.63 | 5937439.25 | 7750963.15 | 7750963.15
Max | 0 | 0 | 4406250.63 | 5937439.25 | 5937439.25 | 7750963.15 | 7750963.15 | 7750963.15 | 7750963.15 | 2261093.3 | 4406250.63 | 4406250.63 | 5937439.25 | 7750963.15 | 7750963.15
Average | 0 | 0 | 4406250.63 | 5937439.25 | 5937439.25 | 7750963.15 | 7750963.15 | 7750963.15 | 7750963.15 | 2261093.3 | 4406250.63 | 4406250.63 | 5937439.25 | 7750963.15 | 7750963.15
Total | 0 | 0 | 4406250.63 | 5937439.25 | 5937439.25 | 7750963.15 | 7750963.15 | 7750963.15 | 7750963.15 | 2261093.3 | 4406250.63 | 4406250.63 | 5937439.25 | 7750963.15 | 7750963.15
Solar Spilled
Min | 0 | 0 | 115935.97 | 845840.65 | 845840.65 | 3554503.35 | 3554503.35 | 3554503.35 | 3554503.35 | 0 | 115935.97 | 115935.97 | 845840.65 | 3554503.35 | 3554503.35
Max | 0 | 0 | 115935.97 | 845840.65 | 845840.65 | 3554503.35 | 3554503.35 | 3554503.35 | 3554503.35 | 0 | 115935.97 | 115935.97 | 845840.65 | 3554503.35 | 3554503.35
Average | 0 | 0 | 115935.97 | 845840.65 | 845840.65 | 3554503.35 | 3554503.35 | 3554503.35 | 3554503.35 | 0 | 115935.97 | 115935.97 | 845840.65 | 3554503.35 | 3554503.35
Total | 0 | 0 | 115935.97 | 845840.65 | 845840.65 | 3554503.35 | 3554503.35 | 3554503.35 | 3554503.35 | 0 | 115935.97 | 115935.97 | 845840.65 | 3554503.35 | 3554503.35
Wind Generated
Min | 0 | 0 | 0 | 0 | 6231037.25 | 0 | 0 | 5914777.99 | 5910247.7 | 24310473.82 | 22849020.25 | 22683547.33 | 21870194 | 20450480.68 | 20222367.32
Max | 0 | 0 | 0 | 0 | 6231037.25 | 0 | 0 | 5914777.99 | 5910247.7 | 24310473.82 | 22849020.25 | 22683547.33 | 21870194 | 20450480.68 | 20222367.32
Average | 0 | 0 | 0 | 0 | 6231037.25 | 0 | 0 | 5914777.99 | 5910247.7 | 24310473.82 | 22849020.25 | 22683547.33 | 21870194 | 20450480.68 | 20222367.32
Total | 0 | 0 | 0 | 0 | 6231037.25 | 0 | 0 | 5914777.99 | 5910247.7 | 24310473.82 | 22849020.25 | 22683547.33 | 21870194 | 20450480.68 | 20222367.32
Wind Spilled
Min | 0 | 0 | 0 | 0 | 642145.71 | 0 | 0 | 1080747.92 | 1081136.25 | 10074934.58 | 11618782.8 | 11592064.42 | 12883929.41 | 14103383.94 | 14068126.61
Max | 0 | 0 | 0 | 0 | 642145.71 | 0 | 0 | 1080747.92 | 1081136.25 | 10074934.58 | 11618782.8 | 11592064.42 | 12883929.41 | 14103383.94 | 14068126.61
Average | 0 | 0 | 0 | 0 | 642145.71 | 0 | 0 | 1080747.92 | 1081136.25 | 10074934.58 | 11618782.8 | 11592064.42 | 12883929.41 | 14103383.94 | 14068126.61
Total | 0 | 0 | 0 | 0 | 642145.71 | 0 | 0% | 1080747.92 | 1081136.25 | 10074934.58 | 11618782.8 | 11592064.42 | 12883929.41 | 14103383.94 | 14068126.61
Weight
Fixed Weight | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Variable Weight | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Weight | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
Volume
Fixed Volume | 0% | 0% | 0% | 0% | 0 | 0 | 0% | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0
Variable Volume | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Volume | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Load | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
Aggregated | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Min | 54% | 54% | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54
Average | 16953% | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53
Max | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54
Tier (Only)
Load Service
Priority
Overall
Overall Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Total Load Served | 3712791500% | 3712791097% | 3712791117% | 3712791020% | 3712791270% | 3712791262% | 3712791928% | 3712790014% | 3712793204% | 3712792368% | 3712792272% | 3712793284% | 3712792880% | 3712792089% | 3712793685%
Total Load Not Served | 2718% | 3121% | 3101% | 3198% | 2948% | 2956% | 2290% | 4204% | 1014% | 1851% | 1946% | 934% | 1339% | 2129% | 533%
Post-Startup
Post-Startup Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DBT Occurrences w/ Post-Startup Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Post-Startup Load Served | 3712791500% | 3712790750% | 3712791117% | 3712791020% | 3712790984% | 3712791262% | 3712791581% | 3712789728% | 3712792847% | 3712792037% | 3712791942% | 3712792919% | 3712792549% | 3712791759% | 3712793285%
Total Post-Startup Load Not Served | 2657% | 3037% | 3040% | 3137% | 2803% | 2894% | 2206% | 4059% | 940% | 1749% | 1845% | 867% | 1237% | 2028% | 501%
Startup Time
Min | 17% | 117% | 17% | 17% | 117% | 17% | 117% | 117% | 117% | 117% | 117% | 117% | 117% | 117% | 117%
Max | 17% | 117% | 17% | 17% | 117% | 17% | 117% | 117% | 117% | 117% | 117% | 117% | 117% | 117% | 117%
Average | 17% | 117% | 17% | 17% | 117% | 17% | 117% | 117% | 117% | 117% | 117% | 117% | 117% | 117% | 117%
Renewable Penetration
Min | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
Max | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1
Average | 0% | 0% | 16.26% | 21.51% | 38.53% | 27.43% | 27.43% | 43.24% | 43.19% | 74.68% | 76.78% | 76.44% | 78.49% | 79.71% | 0.7921
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= 0.00% | 0% | 0% | 50.9% | 50.9% | 4.47% | 50.9% | 50.9% | 3.58% | 3.46% | 4.47% | 4.3% | 4.62% | 3.98% | 3.93% | 0.0472
<= 25.00% | 0% | 0% | 26.33% | 21.17% | 38.17% | 16.21% | 16.21% | 36.32% | 36.57% | 12.47% | 10.97% | 11.02% | 10.04% | 9.58% | 0.0938
<= 50.00% | 0% | 0% | 9.18% | 8.69% | 30.1% | 7.39% | 7.39% | 27.24% | 27.19% | 7.7% | 7.03% | 7.04% | 6.59% | 5.85% | 0.0575
<= 75.00% | 0% | 0% | 6.37% | 5.64% | 8.8% | 4.99% | 4.99% | 8.07% | 8.02% | 8.93% | 8.77% | 8.7% | 8.12% | 7.67% | 7.57%
<= 100.00% | 0% | 0% | 7.22% | 13.59% | 18.46% | 20.51% | 20.51% | 24.79% | 24.76% | 66.42% | 68.94% | 68.62% | 71.26% | 72.97% | 72.58%
<= 110.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 120.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= 130.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 140.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Diesel Fuel Use
Min | 2765970 | 2765970 | 2468130 | 2349870 | 1933770 | 2209710 | 2207520 | 1815510 | 1815510 | 838770 | 786210 | 797160 | 742410 | 707370 | 724890
Max | 2765970 | 2765970 | 2468130 | 2349870 | 1933770 | 2209710 | 2207520 | 1815510 | 1815510 | 838770 | 786210 | 797160 | 742410 | 707370 | 724890
Average | 2765970 | 2765970 | 2468130 | 2349870 | 1933770 | 2209710 | 2207520 | 1815510 | 1815510 | 838770 | 786210 | 797160 | 742410 | 707370 | 724890
Natural Gas Use
Min | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Max | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Average | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Spinning Reserve
Min | 2.26% | 2.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Max | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Average | 41.03% | 41% | 48.84% | 51.86% | 61.01% | 55.33% | 55.28% | 63.87% | 63.82% | 84.5% | 85.71% | 85.42% | 86.64% | 87.29% | 87.02%
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 0.00% | 0% | 0% | 0% | 0% | 0% | 0.01% | 0.01% | 0.03% | 0.02% | 0.03% | 0.04% | 0.07% | 0.05% | 0.07% | 0.0006
<= 5.00% | 0.01% | 0.01% | 0.01% | 0.01% | 0% | 0.01% | 0.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
<= 10.00% | 0.06% | 0.06% | 0.03% | 0.03% | 0.01% | 0.03% | 0.03% | 0.01% | 0.01% | 0% | 0% | 0% | 0% | 0% | 0
<= 15.00% | 0.29% | 0.29% | 0.22% | 0.21% | 0.05% | 0.19% | 0.19% | 0.05% | 0.04% | 0.01% | 0.01% | 0.01% | 0.01% | 0.01% | 0.0002
<= 20.00% | 2.21% | 2.2% | 1.98% | 1.92% | 0.52% | 1.83% | 1.85% | 0.48% | 0.48% | 0.22% | 0.22% | 0.24% | 0.2% | 0.21% | 0.24%
<= 25.00% | 5.01% | 5.01% | 4.52% | 0.0433 | 1.49% | 4.12% | 0.0417 | 0.0142 | 0.0144 | 0.0073 | 0.71% | 0.74% | 0.67% | 0.66% | 0.72%
<= 30.00% | 9.25% | 0.0922 | 0.0796 | 0.0753 | 0.0306 | 0.0723 | 0.0727 | 0.0295 | 0.0298 | 0.0152 | 1.5% | 1.54% | 1.42% | 1.38% | 0.0144
<= 40.00% | 0.2901 | 0.2894 | 0.2385 | 22.56% | 0.1164 | 0.2107 | 21.21% | 10.98% | 11.03% | 4.88% | 4.52% | 4.74% | 4.39% | 4.36% | 0.0444
<= 50.00% | 0.3137 | 31.62% | 23.18% | 22.5% | 17.54% | 21.02% | 20.86% | 16.15% | 16.15% | 5.39% | 4.74% | 4.91% | 4.47% | 4.36% | 0.0459
<= 75.00% | 22.76% | 22.62% | 25.45% | 22.68% | 41.08% | 20.13% | 20.08% | 37.45% | 37.42% | 14.18% | 12.76% | 12.72% | 11.58% | 10.45% | 10.43%
<= 100.00% | 0.04% | 0.04% | 12.81% | 18.25% | 24.61% | 24.36% | 24.34% | 30.5% | 30.42% | 73.04% | 75.49% | 75.03% | 77.19% | 78.49% | 78.05%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0
Diesel Gen Set Data
JD 6619 Run Time (hours/year) | 3359.312 | 3344.7556 | 3701.754 | 3588.6668 | 3378.2972 | 3582.5164 | 3626.1732 | 3332.6288 | 3292.8288 | 3451.3368 | 3343.1708 | 3423.9968 | 3379.998 | 3437.906 | 3396.6304
CAT 3406 Run Time (hours/year) | 6893.3908 | 6819.452 | 6055.154 | 5926.124 | 5561.618 | 5883.0344 | 5907.7988 | 5701.3424 | 5679.134 | 4944.5848 | 4939.376 | 4902.3124 | 4927.3092 | 4882.252 | 4961.1636
SD 60 Run Time (hours/year) | 376.5576 | 456.25 | 216.1148 | 366.4172 | 257.1404 | 325.4644 | 313.4964 | 280.7092 | 291.364 | 851.3304 | 909.3864 | 851.2224 | 881.1272 | 905.5564 | 850.8976
CMS K19G2 Run Time (hours/year) | 0.01 | 7.1344 | 15.8824 | 3.6296 | 0.0204 | 9.4968 | 10.128 | 9.7896 | 0.0096 | 4.1176 | 4.8288 | 3.608 | 7.7476 | 7.7928 | 5.2284
Total Run Time | 10629.2704 | 10627.592 | 9988.9052 | 9884.8376 | 9197.076 | 9800.512 | 9857.5964 | 9324.47 | 9263.3364 | 9251.3696 | 9196.762 | 9181.1396 | 9196.182 | 9233.5072 | 9213.92
JD 6619 Run Time (hours) | 83982.8 | 83618.89 | 92543.85 | 89716.67 | 84457.43 | 89562.91 | 90654.33 | 83315.72 | 82320.72 | 86283.42 | 83579.27 | 85599.92 | 84499.95 | 85947.65 | 84915.76
CAT 3406 Run Time (hours) | 172334.77 | 170486.3 | 151378.85 | 148153.1 | 139040.45 | 147075.86 | 147694.97 | 142533.56 | 141978.35 | 123614.62 | 123484.4 | 122557.81 | 123182.73 | 122056.3 | 124029.09
SD 60 Run Time (hours) | 9413.94 | 11406.25 | 5402.87 | 9160.43 | 6428.51 | 8136.61 | 7837.41 | 7017.73 | 7284.1 | 21283.26 | 22734.66 | 21280.56 | 22028.18 | 22638.91 | 21272.44
CMS K19G2 Run Time (hours) | 0.25 | 178.36 | 397.06 | 90.74 | 0.51 | 237.42 | 253.2 | 244.74 | 0.24 | 102.94 | 120.72 | 90.2 | 193.69 | 194.82 | 130.71
Total Run Time | 265731.76 | 265689.8 | 249722.63 | 247120.94 | 229926.9 | 245012.8 | 246439.91 | 233111.75 | 231583.41 | 231284.24 | 229919.05 | 229528.49 | 229904.55 | 230837.68 | 230348
Assumptions
Horizon (years) | 25
Nominal Discount Rate | 3%
Load Inflation Rate | 1%
Fuel Cost Adjustment | 1
Heating fuel cost ($/gal) | 7.99
Diesel oil cost ($/gal) | 7.1633
HHV (Btu/gallon) | 134000
Conversion (kWh/Btu) | 0.00029307
Baseline total fuel use (gal/year) | 186075.5898
Baseline Gen O&M net present cost | -2655676.211
Baseline diesel fuel net present cost | -13815874.8773
Baseline heating fuel net present cost | -6752037.5899
Baseline total net present cost | 21141875662.7895
Energy Efficiency Cost Electrical Curve | 0.1493
Energy Efficiency Cost Electrical Curve | -0.9009
Energy Efficiency Cost Electrical Curve | 16.515
Energy Efficiency Cost Thermal Curve | 0.1123
Energy Efficiency Cost Thermal Curve | -0.6774
Energy Efficiency Cost Thermal Curve | 12.418
Baseline electrical load (kWh/year) | 1747196.0752
Baseline thermal load (kWh/year) | 2813162.6652
EE electrical load(kWh/year) | 1485116.6
EE thermal load(kWh/year) | 1547239.44
Assumed replacement usage (hours) | 80000
Gen replacement curve ($/kW) | 410.53
Gen replacement curve ($) | 105.26
202kW Gen O&M | 15.7808
314kW Gen O&M | 16.4528
365kW Gen O&M | 16.7588
397kW Gen O&M | 17.1422
Wind Replacement cost (First turbine) | 560000
Wind O&M Cost ($/kWh) | 17500
Solar O&M Cost ($/hour/100kW) | 0.54
EE electrical load reduction (%) | 0.15
EE thermal load reduction (%) | 0.45
EE electrical load reduction cost ($/kWh/year) | 0.38575
EE thermal load reduction cost ($/kWh/year) | 2.3221
EE electrical load reduction cost ($/kWh/year) | -101097.8516
EE thermal load reduction cost ($/kWh/year) | -2939619.4323 | -3040717.2839
Financial calculations
RE Purchase Cost | 0 | -120000 | -1050000 | -1550000 | -2500000 | -2550000 | -2670000 | -3500000 | -3620000 | -4300000 | -4800000 | -4885000 | -5300000 | -6300000 | -6420000
Stove Cost | 0 | 0 | -10264.69 | -11931.14 | -13397.23 | -18115.3 | -18115.3 | -20582.77 | -20583.65 | -33002.13 | -36791.6 | -36730.59 | -41346.51 | -50314.81 | -50234.31
kW of Stoves | 0 | 0 | 0.52938 | 3.8623 | 6.7945 | 16.2306 | 16.2306 | 21.1655 | 21.1673 | 46.0043 | 53.5832 | 53.4612 | 62.693 | 80.6296 | 80.4686
# of Stoves | 0 | 0 | 1 | 1 | 2 | 3 | 3 | 4 | 4 | 8 | 9 | 9 | 11 | 14 | 14
Gen Replacement Cost (per year)
JD 6619 | -3486.6434 | -3471.5352 | -3842.0653 | -3724.6916 | -3506.3482 | -3718.3081 | -3763.6197 | -3458.9488 | -3417.6402 | -3582.1563 | -3469.8903 | -3553.78 | -3508.1134 | -3568.2164 | -3525.3763
CAT 3406 | -11116.5991 | -10997.362 | -9764.8199 | -9556.7402 | -8968.921 | -9487.2519 | -9527.1881 | -9194.247 | -9158.4327 | -7973.8649 | -7965.4649 | -7905.6945 | -7946.0055 | -7873.3442 | -8000.6006
SD 60 | -705.8041 | -855.1762 | -405.0767 | -686.7973 | -481.9734 | -610.0371 | -587.6048 | -526.1498 | -546.1207 | -1595.6987 | -1704.5165 | -1595.4963 | -1651.5486 | -1697.3377 | -1594.8875
CMS | -0.020386 | -14.544 | -32.3774 | -7.3992 | -0.041587 | -19.3599 | -20.6466 | -19.9568 | -0.01957 | -8.394 | -9.8439 | -7.3552 | -15.794 | -15.8862 | -10.6585
New Small (100kW) Gen (purchase) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Gen O&M Cost (per year)
JD 6619 | -53012.4628 | -52782.7519 | -58416.4544 | -56631.8536 | -53312.0635 | -56534.7957 | -57223.7327 | -52591.3819 | -51963.3081 | -54464.6832 | -52757.7426 | -54033.2375 | -53338.9034 | -54252.7351 | -53601.3752
CAT 3406 | -113415.2355 | -112198.7389 | -99623.935 | -97501.0366 | -91503.9105 | -96792.0942 | -97199.5367 | -93802.7612 | -93437.3719 | -81352.0176 | -81266.3185 | -80656.5203 | -81067.7864 | -80326.4716 | -81624.7844
SD 60 | -6310.6347 | -7646.1797 | -3621.8139 | -6140.6943 | -4309.3517 | -5454.3765 | -5253.8078 | -4704.3353 | -4882.8964 | -14267.2333 | -15240.1793 | -14265.4234 | -14766.5905 | -15175.9933 | -14259.9802
CMS | -0.17142 | -122.2996 | -272.26 | -62.2195 | -0.3497 | -162.7965 | -173.6167 | -167.8157 | -0.16457 | -70.5849 | -82.7765 | -61.8492 | -132.8113 | -133.5861 | -89.6265
Deasil Fuel use (Gal/year) | 110638.8 | 110638.8 | 98725.2 | 93994.8 | 77350.8 | 88388.4 | 88300.8 | 72620.4 | 72620.4 | 33550.8 | 31448.4 | 31886.4 | 29696.4 | 28294.8 | 28995.6
Heating Fuel use (Gal/year) | 27538.3177 | 27538.3367 | 28387.8167 | 28092.1977 | 28946.2377 | 25858.3777 | 25858.3777 | 26192.2177 | 26197.8877 | 24719.0677 | 23273.5777 | 23223.2367 | 21402.9867 | 17513.9077 | 17469.0767
Total Fuel usage (Gal/year) | 138177.1177 | 138177.1367 | 127113.0167 | 122086.9977 | 106297.0377 | 114246.7777 | 114159.1777 | 98812.6177 | 98818.2877 | 58269.8677 | 54721.9777 | 55109.6367 | 51099.3867 | 45808.7077 | 46464.6767
New Wind Turbines (#) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 5 | 5 | 5 | 5 | 5 | 5
New 100kW Solar Fields (#) | 0 | 0 | 2 | 3 | 3 | 5 | 5 | 5 | 5 | 1 | 2 | 2 | 3 | 5 | 5
Wind Replacement Cost (per replacement) | 0 | 0 | 0 | 0 | -560000 | 0 | 0 | -560000 | -560000 | -2520000 | -2520000 | -2520000 | -2520000 | -2520000 | -2520000
Wind Replacement NPV (Turbines are replaced every 20 years: this means that the first replacement is out of the time horizon for this analysis and so the replacement cost is not used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Replacement NPV (converter only after 10 years) | 0 | 0 | -126423.7234 | -189635.5851 | -189635.5851 | -316059.3085 | -316059.3085 | -316059.3085 | -316059.3085 | -63211.8617 | -126423.7234 | -126423.7234 | -189635.5851 | -316059.3085 | -316059.3085
Wind O&M Cost per year ($/year) | 0 | 0 | -34562.5 | -51187.5 | -51187.5 | -83125 | -83125 | -83125 | -83125 | -17500 | -34562.5 | -34562.5 | -51187.5 | -83125 | -83125
Solar O&M Cost per year ($/year) | 0 | 0 | -9460.8 | -14191.2 | -14191.2 | -23652 | -23652 | -23652 | -23652 | -4730.4 | -9460.8 | -9460.8 | -14191.2 | -23652 | -23652
Gen + Wind + Solar O&M + Genorator Replacement Cost
Year
1 | -188047.5714 | -188088.5876 | -220002.1026 | -239690.1323 | -227461.6596 | -279556.0199 | -280526.7531 | -271242.5965 | -270182.9542 | -185545.0329 | -206520.0325 | -206102.6563 | -227806.2531 | -269820.5705 | -269484.2891
2 | -177252.8715 | -177291.5332 | -207373.0819 | -225930.9382 | -214404.4299 | -263508.3607 | -264423.3698 | -255672.1618 | -254673.3473 | -174893.989 | -194664.9378 | -194271.5207 | -214729.2423 | -254331.766 | -254014.7885
3 | -172090.1665 | -172127.7021 | -201333.0892 | -219350.4254 | -208159.6406 | -255833.3599 | -256721.7183 | -248225.3998 | -247255.677 | -169799.9893 | -188995.0852 | -188613.1269 | -208474.9925 | -246924.0446 | -246616.2995
4 | -167077.8315 | -167114.2739 | -195469.0186 | -212961.5781 | -202096.7385 | -248381.9028 | -249244.3867 | -240995.5338 | -240054.0554 | -164854.3585 | -183490.374 | -183119.5407 | -202402.9053 | -239732.0822 | -239433.3005
5 | -162211.4869 | -162246.8679 | -189775.7462 | -206758.8137 | -196210.4257 | -241147.4785 | -241984.8414 | -233976.2464 | -233062.1897 | -160052.7753 | -178145.9942 | -177785.9618 | -196507.6751 | -232749.5943 | -232459.515
6 | -157486.8805 | -157521.2309 | -184248.2973 | -200736.7123 | -190495.559 | -234123.7655 | -234936.7393 | -227161.4043 | -226273.9706 | -155391.044 | -172957.2759 | -172607.7299 | -190784.1506 | -225970.4799 | -225688.8496
7 | -152899.884 | -152933.2339 | -178881.8421 | -194890.0119 | -184947.1446 | -227304.6267 | -228093.9216 | -220545.0527 | -219683.4666 | -150865.0912 | -167919.6854 | -167580.3203 | -185227.3307 | -219388.8155 | -219115.3879
8 | -148446.4893 | -148478.8679 | -173671.6913 | -189213.6038 | -179560.3346 | -220684.1036 | -221450.4093 | -214121.4104 | -213284.919 | -146470.9624 | -163028.8207 | -162699.3401 | -179832.3599 | -212998.85 | -212733.3863
9 | -144122.8052 | -144154.2407 | -168613.2925 | -183702.528 | -174330.4219 | -214256.4113 | -215000.3974 | -207884.8645 | -207072.7369 | -142204.8178 | -158280.4085 | -157960.5244 | -174594.5241 | -206795 | -206537.2683
10 | -139925.0536 | -139955.5735 | -163702.2258 | -178351.9689 | -169252.8368 | -208015.9333 | -208738.2499 | -201829.9655 | -201041.4921 | -138062.9299 | -153670.2995 | -153359.7324 | -169509.2467 | -200771.8446 | -200521.6197
11 | -135849.5666 | -135879.1975 | -158934.1998 | -173157.2514 | -164323.1425 | -201957.2168 | -202658.4951 | -195951.4228 | -195185.9147 | -134041.6795 | -149194.4655 | -148892.9441 | -164572.0842 | -194924.121 | -194681.1842
12 | -131892.7831 | -131921.551 | -154305.0483 | -168113.8363 | -159537.0316 | -196074.9677 | -196755.8205 | -190244.0998 | -189500.888 | -130137.5529 | -144848.9957 | -144556.2564 | -159778.7225 | -189246.7194 | -189010.8584
13 | -128051.2457 | -128079.1757 | -149810.7265 | -163217.3168 | -154890.3219 | -190364.0463 | -191025.0684 | -184703.0095 | -183981.4447 | -126347.1388 | -140630.0929 | -140345.88 | -155124.9733 | -183734.679 | -183505.6878
14 | -124321.5978 | -124348.7143 | -145447.3073 | -158463.4143 | -150378.9533 | -184819.4625 | -185461.2315 | -179323.3102 | -178622.7618 | -122667.125 | -136534.0707 | -136258.1359 | -150606.7702 | -178383.1835 | -178160.8619
15 | -120700.5804 | -120726.9071 | -141210.978 | -153847.9751 | -145998.9838 | -179436.3713 | -180059.448 | -174100.3012 | -173420.1571 | -119094.2961 | -132557.3502 | -132289.4524 | -146220.1653 | -173187.5568 | -172971.7106
16 | -117185.0295 | -117210.5894 | -137098.0369 | -149366.9661 | -141746.5862 | -174210.0692 | -174814.9981 | -169029.4186 | -168369.0846 | -115625.5302 | -128696.4565 | -128436.3615 | -141961.3255 | -168143.2591 | -167933.6996
17 | -113771.8733 | -113796.6888 | -133104.8902 | -145016.472 | -137618.0449 | -169135.9896 | -169723.2991 | -164106.2317 | -163465.1307 | -112257.7964 | -124948.0161 | -124695.4966 | -137826.5296 | -163245.8826 | -163042.4268
18 | -110458.1294 | -110482.2221 | -129228.0487 | -140792.6912 | -133609.7523 | -164209.6986 | -164779.902 | -159326.4385 | -158704.0104 | -108988.1518 | -121308.7535 | -121063.5889 | -133812.1647 | -158491.1481 | -158293.6183
19 | -107240.9023 | -107264.2933 | -125464.125 | -136691.9332 | -129718.2061 | -159426.8918 | -159980.4874 | -154685.8626 | -154081.5635 | -105813.7396 | -117775.4888 | -117537.465 | -129914.723 | -153874.9011 | -153683.1245
20 | -104117.3809 | -104140.0906 | -121809.8301 | -132710.6148 | -125940.006 | -154783.3901 | -155320.8616 | -150180.4492 | -149593.7509 | -102731.786 | -114345.1348 | -114114.0437 | -126130.799 | -149393.1079 | -149206.917
Total Gen O&M + Replacement Cost | -2803150.1292 | -2803761.5415 | -3279483.5782 | -3572965.1837 | -3390680.22 | -4167230.066 | -4181700.3984 | -4043305.18 | -4027509.5151 | -2807004.0467 | -3119669.9983 | -3113448.3383 | -3436975.1976 | -4063265.8661 | -4058253.0536
Diesel Fuel Cost
Year
1 | -792542.604 | -792542.604 | -707201.516 | -673316.084 | -554089.564 | -633155.572 | -632528.064 | -520204.132 | -520204.132 | -240335.564 | -225275.372 | -228412.912 | -212725.212 | -202685.084 | -207705.148
2 | -747047.4163 | -747047.4163 | -666605.2559 | -634664.9863 | -522282.5563 | -596809.852 | -596218.3655 | -490342.2867 | -490342.2867 | -226539.3194 | -212343.6441 | -215301.0764 | -200513.9146 | -191050.131 | -195782.0228
3 | -725288.7537 | -725288.7537 | -647189.5688 | -616179.5984 | -507070.443 | -579427.0408 | -578852.7821 | -476060.4726 | -476060.4726 | -219941.0868 | -206158.8777 | -209030.1713 | -194673.7035 | -185485.5641 | -190079.6338
4 | -704163.8386 | -704163.8386 | -628339.3872 | -598232.6198 | -492301.401 | -562550.525 | -561992.9923 | -462194.6336 | -462194.6336 | -213535.0358 | -200154.2502 | -202941.9139 | -189003.5956 | -180083.0719 | -184543.3338
5 | -683654.2122 | -683654.2122 | -610038.24 | -580808.3687 | -477962.5252 | -546165.5583 | -545624.2644 | -448732.6539 | -448732.6539 | -207315.5687 | -194324.5148 | -197030.9844 | -183498.6365 | -174837.9339 | -179168.2852
6 | -663741.9536 | -663741.9536 | -592270.136 | -563891.6201 | -464041.2866 | -530257.8236 | -529732.2955 | -435662.7708 | -435662.7708 | -201277.2512 | -188664.5775 | -191292.2178 | -178154.016 | -169745.5669 | -173949.7915
7 | -644409.6637 | -644409.6637 | -575019.5495 | -547467.5924 | -450525.521 | -514813.421 | -514303.1995 | -422973.5639 | -422973.5639 | -195414.807 | -183169.4927 | -185720.5998 | -172965.0641 | -164801.5213 | -168883.2927
8 | -625640.4502 | -625640.4502 | -558271.4073 | -531521.9343 | -437403.4185 | -499818.8553 | -499323.4947 | -410653.9455 | -410653.9455 | -189723.1136 | -177834.4589 | -180311.262 | -167927.2467 | -160001.477 | -163964.3618
9 | -607417.9128 | -607417.9128 | -542011.075 | -516040.7129 | -424663.5131 | -485261.0246 | -484780.0919 | -398693.151 | -398693.151 | -184197.1976 | -172654.8145 | -175059.4776 | -163036.1619 | -155341.2398 | -159188.7008
10 | -589726.1289 | -589726.1289 | -526224.3447 | -501010.4009 | -412294.6729 | -471127.2083 | -470660.2834 | -387080.7291 | -387080.7291 | -178832.2307 | -167626.0335 | -169960.6579 | -158287.5358 | -150816.7376 | -154552.1367
11 | -572549.6397 | -572549.6397 | -510897.422 | -486417.865 | -400286.0902 | -457405.0566 | -456951.7315 | -375806.5331 | -375806.5331 | -173623.525 | -162743.7218 | -165010.3475 | -153677.2192 | -146424.0171 | -150050.6182
12 | -555873.4366 | -555873.4366 | -496016.9146 | -472250.3543 | -388627.272 | -444082.5792 | -443642.4577 | -364860.7118 | -364860.7118 | -168566.5291 | -158003.6134 | -160204.2209 | -149201.1837 | -142159.2399 | -145680.2118
13 | -539682.9482 | -539682.9482 | -481569.82 | -458495.4896 | -377308.0311 | -431148.1352 | -430720.8328 | -354233.7008 | -354233.7008 | -163656.8244 | -153401.5664 | -155538.0785 | -144855.5182 | -138018.6795 | -141437.0989
14 | -523964.0274 | -523964.0274 | -467543.5145 | -445141.2521 | -366318.4768 | -418590.4225 | -418175.5658 | -343916.2143 | -343916.2143 | -158890.1207 | -148933.5596 | -151007.8432 | -140636.4254 | -133998.718 | -137317.5717
15 | -508702.9392 | -508702.9392 | -453925.7423 | -432175.9729 | -355649.0066 | -406398.4684 | -405995.6949 | -333899.2372 | -333899.2372 | -154262.2531 | -144595.689 | -146609.5565 | -136540.2188 | -130095.8427 | -133318.0308
16 | -493886.3487 | -493886.3487 | -440704.6041 | -419588.3232 | -345290.2977 | -394561.6199 | -394170.5776 | -324174.0167 | -324174.0167 | -149769.1778 | -140384.1641 | -142339.3752 | -132563.3193 | -126306.6434 | -129434.9813
17 | -479501.3095 | -479501.3095 | -427868.5477 | -407367.3041 | -335233.2987 | -383069.5338 | -382689.8812 | -314732.0551 | -314732.0551 | -145406.9687 | -136295.3049 | -138193.5682 | -128702.2517 | -122627.8091 | -125665.0304
18 | -465535.2519 | -465535.2519 | -415406.357 | -395502.237 | -325469.222 | -371912.1688 | -371543.574 | -305565.102 | -305565.102 | -141171.8143 | -132325.5387 | -134168.5128 | -124953.6424 | -119056.1254 | -122004.8839
19 | -451975.9727 | -451975.9727 | -403307.1427 | -383982.7543 | -315989.536 | -361079.7755 | -360721.9165 | -296665.1476 | -296665.1476 | -137060.0139 | -128471.3968 | -130260.6921 | -121314.216 | -115588.4712 | -118451.3436
20 | -438811.624 | -438811.624 | -391560.3327 | -372798.7906 | -306785.9572 | -350562.8888 | -350215.4529 | -288024.4151 | -288024.4151 | -133067.9747 | -124729.5115 | -126466.6913 | -117780.7922 | -112221.8167 | -115001.3045
Total Diesel Fuel Cost | -11814116.432 | -11814116.432 | -10541970.878 | -10036854.2609 | -8259592.0898 | -9438197.5296 | -9428843.5182 | -7754475.4728 | -7754475.4728 | -3582586.3765 | -3358090.1022 | -3404860.1593 | -3171009.8737 | -3021345.6908 | -3096177.7823
Heating Fuel Cost
Year
1 | -220031.1585 | -220031.3102 | -226818.6554 | -224456.6597 | -231280.4393 | -206608.4379 | -206608.4379 | -209275.8195 | -209321.1228 | -197505.351 | -185955.8859 | -185553.6612 | -171009.8637 | -139936.1226 | -139577.9228
2 | -207400.4699 | -207400.6129 | -213798.3367 | -211571.9292 | -218003.996 | -194748.2684 | -194748.2684 | -197262.5314 | -197305.2341 | -186167.7359 | -175281.2574 | -174902.122 | -161193.1979 | -131903.2167 | -131565.579
3 | -201359.6795 | -201359.8183 | -207571.2007 | -205409.64 | -211654.365 | -189075.9887 | -189075.9887 | -191517.0208 | -191558.4797 | -180745.3747 | -170175.978 | -169807.8854 | -156498.2504 | -128061.3755 | -127733.5719
4 | -195494.8345 | -195494.9692 | -201525.4375 | -199426.835 | -205489.6748 | -183568.9211 | -183568.9211 | -185938.8551 | -185979.1065 | -175480.9463 | -165219.3961 | -164862.0247 | -151940.049 | -124331.4325 | -124013.1766
5 | -189800.8102 | -189800.941 | -195655.7646 | -193618.2864 | -199504.5386 | -178222.2535 | -178222.2535 | -180523.1603 | -180562.2393 | -170369.8508 | -160407.1807 | -160060.2181 | -147514.6106 | -120710.1286 | -120401.1423
6 | -184272.6313 | -184272.7583 | -189957.053 | -187978.9188 | -193693.7268 | -173031.3141 | -173031.3141 | -175265.2042 | -175303.145 | -165407.6221 | -155735.1269 | -155398.27 | -143218.0686 | -117194.2997 | -116894.3129
7 | -178905.4672 | -178905.5906 | -184424.3233 | -182503.8047 | -188052.162 | -167991.5671 | -167991.5671 | -170160.3924 | -170197.2281 | -160589.9244 | -151199.1523 | -150872.1068 | -139046.6685 | -113780.8734 | -113489.6242
8 | -173694.6284 | -173694.7481 | -179052.7411 | -177188.1599 | -182574.9145 | -163098.6088 | -163098.6088 | -165204.2645 | -165240.0273 | -155912.5479 | -146795.2935 | -146477.7736 | -134996.7656 | -110466.8674 | -110184.1012
9 | -168635.5615 | -168635.6778 | -173837.6127 | -172027.3397 | -177257.1986 | -158348.1639 | -158348.1639 | -160392.4898 | -160427.211 | -151371.4058 | -142519.7025 | -142211.4307 | -131064.8209 | -107249.3858 | -106974.8555
10 | -163723.8462 | -163723.959 | -168774.3813 | -167016.8347 | -172094.3675 | -153736.0814 | -153736.0814 | -155720.8639 | -155754.5738 | -146962.5299 | -138368.6432 | -138069.3502 | -127247.399 | -104125.6173 | -103859.083
11 | -158955.1904 | -158955.3 | -163858.6226 | -162152.2667 | -167081.9102 | -149258.3315 | -149258.3315 | -151185.3047 | -151218.0328 | -142682.0678 | -134338.4885 | -134047.9128 | -123541.164 | -101092.8324 | -100834.0612
12 | -154325.4276 | -154325.534 | -159086.0413 | -157429.3851 | -162215.4468 | -144911.0014 | -144911.0014 | -146781.8492 | -146813.6241 | -138526.2794 | -130425.717 | -130143.6047 | -119942.8777 | -98148.3809 | -97897.1468
13 | -149830.5122 | -149830.6155 | -154452.4673 | -152844.0632 | -157490.7251 | -140690.2927 | -140690.2927 | -142506.6497 | -142537.4991 | -134491.5334 | -126626.9097 | -126353.0142 | -116449.3958 | -95289.6902 | -95045.7736
14 | -145466.5167 | -145466.617 | -149953.8518 | -148392.2944 | -152903.6166 | -136592.5172 | -136592.5172 | -138355.9706 | -138385.9214 | -130574.3043 | -122938.7473 | -122672.8294 | -113057.6659 | -92514.2624 | -92277.4501
15 | -141229.6279 | -141229.7253 | -145586.2639 | -144070.1887 | -148450.1132 | -132614.0943 | -132614.0943 | -134326.1851 | -134355.2635 | -126771.1692 | -119358.0071 | -119099.8343 | -109764.7241 | -89819.6722 | -89589.7573
16 | -137116.1436 | -137116.2381 | -141345.8872 | -139873.9696 | -144126.3235 | -128751.5479 | -128751.5479 | -130413.7719 | -130442.0034 | -123078.8051 | -115881.5603 | -115630.9071 | -106567.6933 | -87203.5652 | -86980.3469
17 | -133122.4695 | -133122.5613 | -137229.0167 | -135799.9705 | -139928.4694 | -125001.5028 | -125001.5028 | -126615.3125 | -126642.7218 | -119493.9855 | -112506.3692 | -112263.0166 | -103463.7799 | -84663.6556 | -84446.9388
18 | -129245.116 | -129245.2051 | -133232.0551 | -131844.6316 | -135852.8829 | -121360.6823 | -121360.6823 | -122927.4879 | -122954.0988 | -116013.5782 | -109229.4847 | -108993.22 | -100450.2718 | -82197.7238 | -81987.3192
19 | -125480.6952 | -125480.7817 | -129351.5098 | -128004.4967 | -131896.0028 | -117825.9052 | -117825.9052 | -119347.0756 | -119372.9115 | -112634.5419 | -106048.0434 | -105818.6602 | -97524.5357 | -79803.6154 | -79599.339
20 | -121825.9176 | -121826.0016 | -125583.9901 | -124276.2104 | -128054.3717 | -114394.0827 | -114394.0827 | -115870.9472 | -115896.0306 | -109353.9242 | -102959.2654 | -102736.5633 | -94684.0153 | -77479.2382 | -77280.9117
Total Heating Fuel Cost | -3279916.7042 | -3279918.9649 | -3381095.2122 | -3345885.8851 | -3447605.2454 | -3079829.5629 | -3079829.5629 | -3119591.1563 | -3120266.4745 | -2944133.4779 | -2771970.209 | -2765974.4053 | -2549175.8179 | -2085971.956 | -2080632.4139
Total Net Present Cost | -20937900.5493 | -21058514.2223 | -21429955.3656 | -21747989.3387 | -20841627.6542 | -22610149.0509 | -22735265.3719 | -21794731.1715 | -21899611.7048 | -16770655.1767 | -17253662.9169 | -17373154.5003 | -17728860.2682 | -18877674.9153 | -19062074.1522
Marginal Net Present Value (NPC-Baseline) | -21162813563.3387 | -21162934177.0118 | -21163305618.1551 | -21163623652.1282 | -21162717290.4437 | -21164485811.8404 | -21164610928.1614 | -21163670393.961 | -21163775274.4942 | -21158646317.9662 | -21159129325.7064 | -21159248817.2898 | -21159604523.0576 | -21160753337.7048 | -21160937736.9416
Net Reduction in Imported Fuel | 25.74% | 25.74% | 31.69% | 34.39% | 42.87% | 38.6% | 38.65% | 46.9% | 46.89% | 68.68% | 70.59% | 70.38% | 72.54% | 75.38% | 75.03%
Marginal NPV = NPC - NPC(baseline) - capital investment | Highest NPV Cases
Marginal NPV (Utility Only) | 1854284.5272 | 1733673.1149 | 1473672.9088 | 1122096.0587 | 2131643.1934 | 64.1842 | -125052.1368 | 857711.127 | 753506.792 | 5718748.8035 | 5067367.2644 | 4941818.8673 | 4373930.432 | 2770880.2229 | 2581060.944
Marginal NPV (Heating Customers Only) | 532501.4534 | 532499.1927 | 421058.2554 | 454601.1325 | 351415.6822 | 714473.2948 | 714473.2948 | 672244.2313 | 671568.0331 | 835282.5497 | 1003656.3486 | 1009713.1623 | 1221895.8297 | 1676131.3916 | 1681551.4337
Total Marginal NPV | 2386785.9806 | 2266172.3076 | 1894731.1642 | 1576697.1912 | 2483058.8756 | 714537.479 | 589421.158 | 1529955.3583 | 1425074.8251 | 6554031.3532 | 6071023.613 | 5951532.0296 | 5595826.2617 | 4447011.6145 | 4262612.3777
Total % ROI | 178.5% | 171.7% | 146.2% | 134.3% | 144.7% | 112.7% | 110.3% | 123.3% | 121.3% | 188.9% | 177.1% | 174.7% | 166.8% | 147.4% | 144.8%
Normalized to Energy Efficient System
Normalized NPV (Utility Only) |  | -120611.4123 | -380611.6184 | -732188.4685 | 277358.6663 | -1854220.3429 | -1979336.6639 | -996573.4002 | -1100777.7352 | 3864464.2763 | 3213082.7372 | 3087534.3401 | 2519645.9048 | 916595.6958 | 726776.4168
Normalized NPV (Heating Customers Only) |  | -2.2608 | -111443.198 | -77900.3209 | -181085.7713 | 181971.8413 | 181971.8413 | 139742.7779 | 139066.5797 | 302781.0963 | 471154.8951 | 477211.7089 | 689394.3763 | 1143629.9382 | 1149049.9803
Normalized Total NPV |  | -120613.673 | -492054.8164 | -810088.7894 | 96272.895 | -1672248.5016 | -1797364.8226 | -856830.6223 | -961711.1555 | 4167245.3726 | 3684237.6324 | 3564746.049 | 3209040.2811 | 2060225.6339 | 1875826.3971
Normalized % ROI |  | -0.5114% | 53.59% | 48.14% | 103.8% | 34.88% | 33.14% | 75.66% | 73.58% | 196.2% | 176.2% | 172.4% | 160.1% | 132.4% | 129%
No Generator
100kW Diesel
Note on A225: Author: Already Included in Purchase Cost
Note on A234: Author: If the generator utilization is less than 30% then a new small generator is purchased (This assumes that the O&M costs for the generator set would not change as the O&M cost for the new generator would offset some of the O&M cost for the existing generator)
Note on B334: Author: NPV Values are normalized to the Baseline
Note on C334: Author: NPV Values are normalized to the Baseline
Note on D334: Author: NPV Values are normalized to the Baseline
Note on E334: Author: NPV Values are normalized to the Baseline
Note on F334: Author: NPV Values are normalized to the Baseline
Note on G334: Author: NPV Values are normalized to the Baseline
Note on H334: Author: NPV Values are normalized to the Baseline
Note on I334: Author: NPV Values are normalized to the Baseline
Note on J334: Author: NPV Values are normalized to the Baseline
Note on K334: Author: NPV Values are normalized to the Baseline
Note on L334: Author: NPV Values are normalized to the Baseline
Note on M334: Author: NPV Values are normalized to the Baseline
Note on N334: Author: NPV Values are normalized to the Baseline
Note on O334: Author: NPV Values are normalized to the Baseline
Note on P334: Author: NPV Values are normalized to the Baseline
Note on A335: Author: Value of Heating Fuel Deferred - Cost of Stove System
Note on B335: Author: NPV Values are normalized to the Baseline
Note on A341: Author: Value of Heating Fuel Deferred - Cost of Stove System

## High-EE no Stoves Detailed
Summary Results
New Solar | No Generator | No Generator | No Generator | SG 100 | SG 100 | No Generator | SG 200 | SG 200 | SG 300 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 200 | SG 200 | SG 300 | SG 300 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | WG 100 | WG 200 | WG 500 | WG 500 | WG 500 | WG 500 | WG 500
New Storage | No Battery | Bat 50/50 | Bat 100/100 | No Battery | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery
New Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel | 100kW Diesel
Energy Efficiency Cost | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196
Renewable Energy Purchase Cost | 0 | -85000 | -120000 | -550000 | -670000 | -950000 | -1050000 | -1170000 | -1550000 | -1670000 | -2500000 | -2550000 | -2670000 | -3500000 | -4285000 | -4800000 | -4885000 | -5300000 | -5385000 | -6300000
Stove Purchase Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Generator Purchase Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Net Reduction in Imported Fuel | 25.65% | 25.65% | 25.65% | 28.5% | 28.54% | 34.56% | 31.54% | 31.54% | 33.84% | 33.88% | 41.97% | 36.55% | 36.55% | 43.95% | 50.77% | 64.09% | 64.02% | 64.62% | 64.29% | 65.7%
Marginal NPV (Utility Only) | 1806858.6998 | 1693636.0512 | 1717764.6934 | 1667326.8968 | 1592223.4948 | 3146506.0868 | 1451040.5573 | 1314381.4135 | 1095659.9392 | 992626.1845 | 2101504.4648 | 117.7631 | -197211.4458 | 773934.893 | 1488816.4957 | 5071352.2428 | 4971580.3442 | 4303561.0466 | 4153359.3798 | 2799122.7051
Marginal NPV (Heating Customers Only) | 511955.2688 | 511941.3178 | 511954.6622 | 465034.7526 | 465029.6574 | 337219.2544 | 398193.4097 | 398188.9211 | 344322.9864 | 344321.4106 | 164596.3931 | 277916.4298 | 277918.6134 | 112282.6597 | -55341.252 | -409870.9459 | -405707.4798 | -428185.1017 | -418074.2601 | -460112.6513
Total Marginal NPV | 2318813.9686 | 2205577.369 | 2229719.3556 | 2132361.6494 | 2057253.1522 | 3483725.3412 | 1849233.967 | 1712570.3347 | 1439982.9256 | 1336947.5951 | 2266100.8579 | 278034.1929 | 80707.1676 | 886217.5527 | 1433475.2437 | 4661481.2969 | 4565872.8644 | 3875375.9449 | 3735285.1198 | 2339010.0538
Total % ROI | 176.3% | 170.6% | 170.5% | 159.4% | 155.4% | 187.3% | 145.2% | 140.7% | 131.4% | 128.4% | 140.9% | 105% | 101.4% | 113.5% | 119.6% | 159.5% | 157.6% | 146.5% | 144.3% | 125%
Total Capital Cost | 3040717.196 | 3125717.196 | 3160717.196 | 3590717.196 | 3710717.196 | 3990717.196 | 4090717.196 | 4210717.196 | 4590717.196 | 4710717.196 | 5540717.196 | 5590717.196 | 5710717.196 | 6540717.196 | 7366875.456 | 7881875.456 | 7966875.456 | 8381875.456 | 8466875.456 | 9381875.456
Raw DATA
Simulation Statistics | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Total Sim Time | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Power Utility Statistics
Failure Statistics
Occurrences | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations") | 1 (all attributed to "Islanded Operations")
Downtime
Min | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Max | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Average | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Total | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0 | 219,0
Thermal Load Service
Overall
Overall Energy Availability | 29.67% | 29.67% | 29.67% | 28.67% | 28.67% | 25.94% | 27.24% | 27.24% | 26.09% | 26.09% | 22.26% | 24.68% | 24.68% | 21.15% | 17.58% | 10.02% | 10.11% | 9.63% | 9.846% | 8.95%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Load Served (kWh) | 11474836 | 11474721 | 11474831 | 11088064 | 11088022 | 10034464 | 10537082 | 10537045 | 10093021 | 10093008 | 8611511 | 9545623 | 9545641 | 8180282 | 6798536 | 3876101 | 3910421 | 3725135 | 3808480 | 3461952
Total Load Not Served (kWh) | 27206150 | 27206264 | 27206154 | 27592922 | 27592964 | 28646522 | 28143904 | 28143941 | 28587964 | 28587958 | 30069475 | 29135363 | 29135345 | 30500703 | 31882450 | 34804885 | 34770565 | 34955851 | 34872505 | 35219033
Post-Startup
Post-Startup Energy Availability
DBT Occurrences w/ Post-Startup Load Loss
Total Post-Startup Load Served | 11474836.32 | 11474721.7 | 11474831.66 | 11088064.33 | 11088022.34 | 10034464.11 | 10537082.46 | 10537045.13 | 10093021.71 | 10093028 | 8611511.07 | 9545623.05 | 9545641.37 | 8180282.82 | 6798536.07 | 3876101.11 | 3910421.49 | 3725135.09 | 3808480.83 | 3461952.74
Total Post-Startup Load Not Served | 27206150.33 | 27206264.95 | 27206154.99 | 27592922.32 | 27592964.31 | 28646522.54 | 28143904.19 | 28143941.52 | 28587964.94 | 28587958.64 | 30069475.58 | 29135363.6 | 29135345.28 | 30500703.83 | 31882450.58 | 34804885.54 | 34770565.16 | 34955851.56 | 34872505.82 | 35219033.91
Variable Selections
New Solar | No Generator | No Generator | No Generator | SG 100 | SG 100 | No Generator | SG 200 | SG 200 | SG 300 | SG 300 | SG 300 | SG 500 | SG 500 | SG 500 | SG 500 | SG 200 | SG 200 | SG 300 | SG 300 | SG 500
Hydro Stand-In | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | No Generator | No Generator | WG 100 | No Generator | No Generator | WG 100 | WG 200 | WG 500 | WG 500 | WG 500 | WG 500 | WG 500
New Storage | No Battery | Bat 50/50 | Bat 100/100 | No Battery | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery | Bat 100/100 | No Battery | No Battery | Bat 100/100 | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery | Bat 50/50 | No Battery
Metric Values
Purchase Cost | 0 | 85000 | 120000 | 550000 | 670000 | 950000 | 1050000 | 1170000 | 1550000 | 1670000 | 2500000 | 2550000 | 2670000 | 3500000 | 4285000 | 4800000 | 4885000 | 5300000 | 5385000 | 6300000
Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Diesel Fuel Used (Gal/Hour) | 12.63 | 12.63 | 12.63 | 11.98 | 11.97 | 10.57 | 11.27 | 11.27 | 10.73 | 10.72 | 8.83 | 10.09 | 10.09 | 8.36 | 6.75 | 3.58 | 3.6 | 3.45 | 3.53 | 3.19
Heating Fuel Deferred (GHFE/Year) | 11687.694 | 11687.5769 | 11687.6889 | 11293.7474 | 11293.7046 | 10220.6032 | 10732.5447 | 10732.507 | 10280.2464 | 10280.2331 | 8771.2544 | 9722.6942 | 9722.7125 | 8332.0261 | 6924.6487 | 3948.0026 | 3982.9593 | 3794.2362 | 3879.1272 | 3526.1712
Average Renewable Energy Spilled | 0 | 0 | 0 | 0 | 0 | 633.75 | 115935.97 | 115935.97 | 845840.65 | 845840.65 | 1479868.96 | 3554503.35 | 3554503.35 | 4593423.99 | 6058992.61 | 11771357.18 | 11782879.47 | 13604052.79 | 13528370.04 | 17732629.14
Diesel Utilization | 0.5854 | 58.57% | 58.57% | 0.5544 | 0.5553 | 0.5091 | 0.5111 | 0.5128 | 0.4845 | 0.4864 | 39.18% | 45.01% | 45.23% | 36.59% | 27.06% | 14.22% | 14.3% | 13.64% | 13.98% | 12.47%
Heating Fuel Deferred from Waste Heat (GHFE/Year) | 11687.694 | 11687.5769 | 11687.6889 | 11293.7474 | 11293.7046 | 10220.6032 | 10732.5447 | 10732.507 | 10280.2464 | 10280.2331 | 8771.2544 | 9722.6942 | 9722.7125 | 8332.0261 | 6924.6487 | 3948.0026 | 3982.9593 | 3794.2362 | 3879.1272 | 3526.1712
Heating Fuel Deferred from Stoves (GHFE/Year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost
Fixed Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Cost | 0 | 85000 | 120000 | 550000 | 670000 | 950000 | 1050000 | 1170000 | 1550000 | 1670000 | 2500000 | 2550000 | 2670000 | 3500000 | 4285000 | 4800000 | 4885000 | 5300000 | 5385000 | 6300000
Total Cost | 0 | 85000 | 120000 | 550000 | 670000 | 950000 | 1050000 | 1170000 | 1550000 | 1670000 | 2500000 | 2550000 | 2670000 | 3500000 | 4285000 | 4800000 | 4885000 | 5300000 | 5385000 | 6300000
Generation
Total Diesel Generation | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278 | 1278
Total Solar Generation | 0 | 0 | 0 | 100 | 100 | 100 | 200 | 200 | 300 | 300 | 300 | 500 | 500 | 500 | 500 | 200 | 200 | 300 | 300 | 500
Total Wind Generation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 200 | 500 | 500 | 500 | 500 | 500
Overall Diesel Efficiency | 34.93% | 34.94% | 34.92% | 34.07% | 34.09% | 33.61% | 31.83% | 31.91% | 30.03% | 30.07% | 27.32% | 27.82% | 27.96% | 25.35% | 21.23% | 10.67% | 10.7% | 10.18% | 10.36% | 9.3%
Overall Diesel Utilization | 58.54% | 58.57% | 58.57% | 55.44% | 55.53% | 50.91% | 51.11% | 51.28% | 48.45% | 48.64% | 39.18% | 45.01% | 45.23% | 36.59% | 27.06% | 14.22% | 14.3% | 13.64% | 13.98% | 12.47%
Solar Generated
Min | 0% | 0% | 0% | 226109330% | 226109330% | 0% | 440625063% | 440625063% | 593743925% | 593743925% | 5937439.25 | 7750963.15 | 7750963.15 | 7750963.15 | 7750963.15 | 4406250.63 | 4406250.63 | 5937439.25 | 5937439.25 | 7750963.15
Max | 0 | 0% | 0% | 226109330% | 226109330% | 0% | 440625063% | 440625063% | 5937439.25 | 593743925% | 5937439.25 | 7750963.15 | 7750963.15 | 7750963.15 | 7750963.15 | 4406250.63 | 4406250.63 | 5937439.25 | 5937439.25 | 7750963.15
Average | 0% | 0% | 0% | 2261093.3 | 2261093.3 | 0 | 4406250.63 | 4406250.63 | 5937439.25 | 5937439.25 | 5937439.25 | 7750963.15 | 7750963.15 | 7750963.15 | 7750963.15 | 4406250.63 | 4406250.63 | 5937439.25 | 5937439.25 | 7750963.15
Total | 0% | 0% | 0% | 2261093.3 | 2261093.3 | 0 | 4406250.63 | 4406250.63 | 5937439.25 | 5937439.25 | 5937439.25 | 7750963.15 | 7750963.15 | 7750963.15 | 7750963.15 | 4406250.63 | 4406250.63 | 5937439.25 | 5937439.25 | 7750963.15
Solar Spilled
Min | 0% | 0 | 0 | 0 | 0 | 0 | 115935.97 | 115935.97 | 845840.65 | 845840.65 | 845840.65 | 3554503.35 | 3554503.35 | 3554503.35 | 3554503.35 | 115935.97 | 115935.97 | 845840.65 | 845840.65 | 3554503.35
Max | 0 | 0 | 0 | 0 | 0 | 0 | 115935.97 | 115935.97 | 845840.65 | 845840.65 | 845840.65 | 3554503.35 | 3554503.35 | 3554503.35 | 3554503.35 | 115935.97 | 115935.97 | 845840.65 | 845840.65 | 3554503.35
Average | 0 | 0 | 0 | 0 | 0 | 0 | 115935.97 | 115935.97 | 845840.65 | 845840.65 | 845840.65 | 3554503.35 | 3554503.35 | 3554503.35 | 3554503.35 | 115935.97 | 115935.97 | 845840.65 | 845840.65 | 3554503.35
Total | 0 | 0 | 0 | 0 | 0 | 0 | 115935.97 | 115935.97 | 845840.65 | 845840.65 | 845840.65 | 3554503.35 | 3554503.35 | 3554503.35 | 3554503.35 | 115935.97 | 115935.97 | 845840.65 | 845840.65 | 3554503.35
Wind Generated
Min | 0 | 0 | 0 | 0 | 0 | 6918540.87 | 0 | 0 | 0 | 0 | 6255250.51 | 0 | 0 | 5701305.59 | 11030118.45 | 22865314.68 | 22804022.86 | 21689240.4 | 21452931.03 | 20588907.15
Max | 0 | 0 | 0 | 0 | 0 | 6918540.87 | 0 | 0 | 0 | 0 | 6255250.51 | 0 | 0 | 5701305.59 | 11030118.45 | 22865314.68 | 22804022.86 | 21689240.4 | 21452931.03 | 20588907.15
Average | 0 | 0 | 0 | 0 | 0 | 6918540.87 | 0 | 0 | 0 | 0 | 6255250.51 | 0 | 0 | 5701305.59 | 11030118.45 | 22865314.68 | 22804022.86 | 21689240.4 | 21452931.03 | 20588907.15
Total | 0 | 0 | 0 | 0 | 0 | 6918540.87 | 0 | 0 | 0 | 0 | 6255250.51 | 0 | 0 | 5701305.59 | 11030118.45 | 22865314.68 | 22804022.86 | 21689240.4 | 21452931.03 | 20588907.15
Wind Spilled
Min | 0 | 0 | 0 | 0 | 0 | 633.75 | 0 | 0 | 0 | 0 | 634028.31 | 0 | 0 | 1038920.64 | 2504489.26 | 11655421.22 | 11666943.5 | 12758212.14 | 12682529.39 | 14178125.79
Max | 0 | 0 | 0 | 0 | 0 | 633.75 | 0 | 0 | 0 | 0 | 634028.31 | 0 | 0 | 1038920.64 | 2504489.26 | 11655421.22 | 11666943.5 | 12758212.14 | 12682529.39 | 14178125.79
Average | 0 | 0 | 0 | 0 | 0 | 633.75 | 0 | 0 | 0 | 0 | 634028.31 | 0 | 0 | 1038920.64 | 2504489.26 | 11655421.22 | 11666943.5 | 12758212.14 | 12682529.39 | 14178125.79
Total | 0 | 0 | 0 | 0 | 0 | 633.75 | 0 | 0 | 0 | 0 | 634028.31 | 0 | 0 | 1038920.64 | 2504489.26 | 11655421.22 | 11666943.5 | 12758212.14 | 12682529.39 | 14178125.79
Weight
Fixed Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Weight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Volume
Fixed Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Volume | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Min | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54
Average | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53 | 169.53
Max | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54 | 339.54
Tier (Only)
Load Service
Priority
Overall
Overall Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DBT Occurrences w/ Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Load Served | 3712791721% | 3712789707% | 3712791815% | 3712790088% | 3712792023% | 3712789460% | 3712790705% | 3712792125% | 3712791750% | 3712792574% | 37127905.55 | 3712791000% | 3712791560% | 37127897.73 | 37127928.39 | 37127921.79 | 37127930.43 | 37127918.12 | 37127931.91 | 37127925.57
Total Load Not Served | 2498% | 4511% | 2404% | 4130% | 2195% | 4759% | 3513% | 2093% | 2468% | 1644% | 36.63 | 32.18 | 26.59 | 44.45 | 13.79 | 20.39 | 11.76 | 24.06 | 10.27 | 16.61
Post-Startup
Post-Startup Energy Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
DBT Occurrences w/ Post-Startup Load Loss | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Total Post-Startup Load Served | 3712791721% | 3712789395% | 3712791468% | 3712790088% | 3712791676% | 3712789174% | 3712790705% | 3712791778% | 3712791750% | 3712792227% | 37127902.69 | 3712791000% | 3712791213% | 37127894.87 | 37127925.06 | 37127918.49 | 37127926.78 | 37127914.82 | 37127928.26 | 37127922.27
Total Post-Startup Load Not Served | 2436% | 4392% | 2319% | 4068% | 2111% | 4613% | 3451% | 2008% | 2406% | 1559% | 35.18 | 31.57 | 25.74 | 43 | 12.81 | 19.38 | 11.09 | 23.05 | 9.6 | 15.6
Startup Time
Min | 17% | 117% | 117% | 0.17 | 1.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Max | 17% | 117% | 117% | 0.17 | 1.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Average | 17% | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 0.17 | 1.17 | 0.17 | 1.17 | 1.17 | 0.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17
Renewable Penetration
Min | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Max | 0% | 0% | 0% | 98.09% | 98.09% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Average | 0% | 0% | 0% | 8.42% | 8.42% | 19.79% | 16.26% | 16.26% | 21.51% | 21.51% | 38.56% | 27.43% | 27.43% | 42.63% | 56.68% | 76.89% | 76.78% | 77.94% | 77.47% | 80.05%
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 0.00% | 0% | 0% | 0% | 50.9% | 50.9% | 7.45% | 50.9% | 50.9% | 50.9% | 50.9% | 3.94% | 50.9% | 50.9% | 4.96% | 5.25% | 4.15% | 4.26% | 4.23% | 4.68% | 3.62%
<= 25.00% | 0% | 0% | 0% | 35.51% | 35.51% | 57.33% | 26.33% | 26.33% | 21.17% | 21.17% | 38.67% | 16.21% | 16.21% | 36.03% | 16.51% | 11% | 11.04% | 10.3% | 10.39% | 9.53%
<= 50.00% | 0% | 0% | 0% | 10.33% | 10.33% | 33.57% | 9.18% | 9.18% | 8.69% | 8.69% | 30.16% | 7.39% | 7.39% | 26.49% | 22.38% | 7.05% | 7.02% | 6.71% | 6.67% | 5.85%
<= 75.00% | 0% | 0% | 0% | 3.14% | 3.14% | 1.6% | 6.37% | 6.37% | 5.64% | 5.64% | 8.79% | 4.99% | 4.99% | 7.9% | 21.16% | 8.76% | 8.72% | 8.13% | 8.06% | 7.69%
<= 100.00% | 0% | 0% | 0% | 0.11% | 0.11% | 0.04% | 7.22% | 7.22% | 13.59% | 13.59% | 18.43% | 20.51% | 20.51% | 24.61% | 34.7% | 69.04% | 68.96% | 70.63% | 70.2% | 73.32%
<= 110.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 120.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 130.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 140.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Diesel Fuel Use
Min | 276615353% | 276624592% | 276596363% | 262279707% | 262227431% | 231429808% | 246848133% | 246849099% | 234966187% | 234850892% | 1933578.93 | 2209001.99 | 2209165.09 | 1830765.66 | 1477288.74 | 784776 | 789153.07 | 755242.88 | 772415.5 | 698316.27
Max | 276615353% | 276624592% | 276596363% | 262279707% | 262227431% | 231429808% | 246848133% | 246849099% | 2349661.87 | 234850892% | 1933578.93 | 2209001.99 | 2209165.09 | 1830765.66 | 1477288.74 | 784776 | 789153.07 | 755242.88 | 772415.5 | 698316.27
Average | 276615353% | 276624592% | 276596363% | 2622797.07 | 2622274.31 | 2314298.08 | 2468481.33 | 2468490.99 | 2349661.87 | 2348508.92 | 1933578.93 | 2209001.99 | 2209165.09 | 1830765.66 | 1477288.74 | 784776 | 789153.07 | 755242.88 | 772415.5 | 698316.27
Natural Gas Use
Min | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Max | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Average | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage | 0 MBTU per outage
Spinning Reserve
Min | 2.7% | 2.7% | 2.7% | 2.7% | 2.7% | 5.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Max | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Average | 41.04% | 40.99% | 41.01% | 44.37% | 44.26% | 49.12% | 48.87% | 48.92% | 51.84% | 51.69% | 60.98% | 55.37% | 55.41% | 63.61% | 73.08% | 85.75% | 85.66% | 86.3% | 86.01% | 87.5%
Histogram (% of DBT Time)
<= -100.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 0.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.01% | 0% | 0.01% | 0.01% | 0.01% | 0.02% | 0.02% | 0.02% | 0.03% | 0.05% | 0.05% | 0.07%
<= 5.00% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
<= 10.00% | 0.04% | 0.04% | 0.03% | 0.05% | 0.05% | 0.02% | 0.03% | 0.02% | 0.02% | 0.02% | 0.02% | 0.02% | 0.02% | 0.02% | 0% | 0% | 0% | 0% | 0% | 0%
<= 15.00% | 0.26% | 0.28% | 0.26% | 0.27% | 0.28% | 0.07% | 0.24% | 0.23% | 0.24% | 0.24% | 0.07% | 0.21% | 0.21% | 0.07% | 0.03% | 0.02% | 0.02% | 0.02% | 0.03% | 0.02%
<= 20.00% | 2.19% | 2.29% | 2.26% | 2.37% | 2.44% | 0.97% | 2.06% | 2.03% | 2.01% | 2.01% | 0.61% | 1.83% | 1.82% | 0.63% | 0.37% | 0.25% | 0.28% | 0.24% | 0.28% | 0.23%
<= 25.00% | 5% | 5.12% | 5.11% | 5% | 5.12% | 2.34% | 4.57% | 4.54% | 4.44% | 4.48% | 1.51% | 4.11% | 4.08% | 1.55% | 1.1% | 0.69% | 0.73% | 0.67% | 0.73% | 0.62%
<= 30.00% | 9.11% | 9.13% | 9.15% | 8.52% | 8.56% | 4.49% | 7.79% | 7.82% | 7.44% | 7.61% | 3.11% | 7.06% | 6.97% | 2.95% | 2.18% | 1.4% | 1.44% | 1.43% | 1.46% | 1.32%
<= 40.00% | 29.08% | 28.78% | 28.99% | 25.59% | 25.56% | 16.38% | 23.75% | 23.68% | 22.54% | 22.78% | 11.49% | 21.08% | 20.93% | 11.07% | 6.47% | 4.42% | 4.5% | 4.45% | 4.61% | 4.15%
<= 50.00% | 31.6% | 31.87% | 31.54% | 25.66% | 25.66% | 26.65% | 23.29% | 23.21% | 22.28% | 22.28% | 17.48% | 21.12% | 21.39% | 16.52% | 7.36% | 4.9% | 4.87% | 4.71% | 4.8% | 4.32%
<= 75.00% | 22.7% | 22.47% | 22.61% | 29.15% | 29.02% | 47.06% | 25.38% | 25.55% | 22.78% | 22.43% | 41.14% | 20.18% | 20.21% | 36.85% | 34.39% | 12.81% | 12.74% | 11.86% | 11.95% | 10.4%
<= 100.00% | 0.02% | 0.02% | 0.04% | 3.38% | 3.3% | 2.02% | 12.9% | 12.91% | 18.24% | 18.15% | 24.57% | 24.37% | 24.36% | 30.33% | 48.08% | 75.48% | 75.39% | 76.57% | 76.1% | 78.87%
<= Infinity | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Diesel Gen Set Data
JD 6619 Run Time (hours/year) | 3305.688 | 3279.6752 | 3408.1756 | 3844.2196 | 3857.0548 | 4023.3272 | 3785.6132 | 3620.1976 | 3629.1092 | 3671.156 | 3431.0984 | 3582.5228 | 3582.4268 | 3286.9336 | 3347.45 | 3464.682 | 3398.6732 | 3434.2688 | 3437.9516 | 3460.5604
CAT 3406 Run Time (hours/year) | 7131.6416 | 7312.9264 | 6926.8772 | 5995.5572 | 5945.06 | 5293.7812 | 6124.6404 | 6207.8616 | 6084.1068 | 6031.2356 | 5551.6736 | 5868.3716 | 6074.6396 | 5720.304 | 5166.1364 | 5002.5924 | 5073.2348 | 4987.494 | 5001.348 | 5095.2688
SD 60 Run Time (hours/year) | 345.2364 | 302.5036 | 358.9964 | 269.6448 | 180.0732 | 192.9252 | 160.996 | 297.0028 | 266.1708 | 261.5492 | 327.6408 | 343.0756 | 421.856 | 374.8964 | 696.2564 | 717.1868 | 698.6528 | 787.956 | 729.7296 | 681.6452
CMS K19G2 Run Time (hours/year) | 18.9316 | 11.2188 | 0.4624 | 0.9988 | 0.0096 | 0.01 | 9.606 | 2.4104 | 9.2156 | 0.0096 | 0.01 | 6.0056 | 5.7428 | 4.498 | 38.6264 | 44.2312 | 39.8148 | 43.8088 | 50.4128 | 36.9008
Total Run Time | 10801.4976 | 10906.324 | 10694.5116 | 10110.4204 | 9982.1976 | 9510.0436 | 10080.8556 | 10127.4724 | 9988.6024 | 9963.9504 | 9310.4228 | 9799.9756 | 10084.6652 | 9386.632 | 9248.4692 | 9228.6924 | 9210.3756 | 9253.5276 | 9219.442 | 9274.3752
JD 6619 Run Time (hours) | 82642.2 | 81991.88 | 85204.39 | 96105.49 | 96426.37 | 100583.18 | 94640.33 | 90504.94 | 90727.73 | 91778.9 | 85777.46 | 89563.07 | 89560.67 | 82173.34 | 83686.25 | 86617.05 | 84966.83 | 85856.72 | 85948.79 | 86514.01
CAT 3406 Run Time (hours) | 178291.04 | 182823.16 | 173171.93 | 149888.93 | 148626.5 | 132344.53 | 153116.01 | 155196.54 | 152102.67 | 150780.89 | 138791.84 | 146709.29 | 151865.99 | 143007.6 | 129153.41 | 125064.81 | 126830.87 | 124687.35 | 125033.7 | 127381.72
SD 60 Run Time (hours) | 8630.91 | 7562.59 | 8974.91 | 6741.12 | 4501.83 | 4823.13 | 4024.9 | 7425.07 | 6654.27 | 6538.73 | 8191.02 | 8576.89 | 10546.4 | 9372.41 | 17406.41 | 17929.67 | 17466.32 | 19698.9 | 18243.24 | 17041.13
CMS K19G2 Run Time (hours) | 473.29 | 280.47 | 11.56 | 24.97 | 0.24 | 0.25 | 240.15 | 60.26 | 230.39 | 0.24 | 0.25 | 150.14 | 143.57 | 112.45 | 965.66 | 1105.78 | 995.37 | 1095.22 | 1260.32 | 922.52
Total Run Time | 270037.44 | 272658.1 | 267362.79 | 252760.51 | 249554.94 | 237751.09 | 252021.39 | 253186.81 | 249715.06 | 249098.76 | 232760.57 | 244999.39 | 252116.63 | 234665.8 | 231211.73 | 230717.31 | 230259.39 | 231338.19 | 230486.05 | 231859.38
Assumptions
Horizon (years) | 25
Nominal Discount Rate | 3%
Load Inflation Rate | 1%
Fuel Cost Adjustment | 1
Heating fuel cost ($/gal) | 7.99
Diesel oil cost ($/gal) | 7.1633
HHV (Btu/gallon) | 134000
Conversion (kWh/Btu) | 0.00029307
Baseline total fuel use (gal/year) | 186075.5898
Baseline Gen O&M net present cost | -2655676.211
Baseline diesel fuel net present cost | -13815874.8773
Baseline heating fuel net present cost | -6752037.5899
Baseline total net present cost | 21141875662.7895
Energy Efficiency Cost Electrical Curve | 0.1493
Energy Efficiency Cost Electrical Curve | -0.9009
Energy Efficiency Cost Electrical Curve | 16.515
Energy Efficiency Cost Thermal Curve | 0.1123
Energy Efficiency Cost Thermal Curve | -0.6774
Energy Efficiency Cost Thermal Curve | 12.418
Baseline electrical load (kWh/year) | 1747196.0752
Baseline thermal load (kWh/year) | 2813162.6652
EE electrical load(kWh/year) | 1485116.6884
EE thermal load(kWh/year) | 1547239.44
Assumed replacement usage (hours) | 80000
Gen replacement curve ($/kW) | 410.53
Gen replacement curve ($) | 105.26
202kW Gen O&M | 15.7808
314kW Gen O&M | 16.4528
365kW Gen O&M | 16.7588
397kW Gen O&M | 17.1422
Wind Replacement cost (First turbine) | 560000
Wind O&M Cost ($/kWh) | 17500
Solar O&M Cost ($/hour/100kW) | 0.54
EE electrical load reduction (%) | 0.15
EE thermal load reduction (%) | 0.45
EE electrical load reduction cost ($/kWh/year) | 0.38575
EE thermal load reduction cost ($/kWh/year) | 2.3221
EE electrical load reduction cost ($/kWh/year) | -101097.7638
EE thermal load reduction cost ($/kWh/year) | -2939619.4323 | -3040717.196
Financial calculations
RE Purchase Cost | 0 | -85000 | -120000 | -550000 | -670000 | -950000 | -1050000 | -1170000 | -1550000 | -1670000 | -2500000 | -2550000 | -2670000 | -3500000 | -4285000 | -4800000 | -4885000 | -5300000 | -5385000 | -6300000
Stove Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kW of Stoves | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
# of Stoves | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gen Replacement Cost (per year)
JD 6619 | -3430.9868 | -3403.988 | -3537.3591 | -3989.9309 | -4003.2526 | -4175.8274 | -3929.1031 | -3757.4176 | -3766.667 | -3810.3075 | -3561.1508 | -3718.3147 | -3718.2151 | -3411.5215 | -3474.3317 | -3596.0073 | -3527.4965 | -3564.4413 | -3568.2637 | -3591.7295
CAT 3406 | -11500.8133 | -11793.1615 | -11170.6008 | -9668.7113 | -9587.2772 | -8536.9951 | -9876.8768 | -10011.0832 | -9811.5105 | -9726.248 | -8952.8842 | -9463.606 | -9796.2433 | -9224.8254 | -8331.1492 | -8067.4106 | -8181.3318 | -8043.0622 | -8065.4038 | -8216.8648
SD 60 | -647.0969 | -567.0003 | -672.8881 | -505.4111 | -337.5218 | -361.6111 | -301.7643 | -556.6898 | -498.8996 | -490.2371 | -614.1164 | -643.0468 | -790.7095 | -702.6904 | -1305.0344 | -1344.2654 | -1309.5261 | -1476.9123 | -1367.7752 | -1277.6477
CMS | -38.5934 | -22.8703 | -0.94264 | -2.0361 | -0.01957 | -0.020386 | -19.5825 | -4.9138 | -18.7867 | -0.01957 | -0.020386 | -12.2428 | -11.7071 | -9.1695 | -78.7427 | -90.1684 | -81.1653 | -89.3073 | -102.7701 | -75.2249
New Small (100kW) Gen (purchase) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26 | -41158.26
Gen O&M Cost (per year)
JD 6619 | -52166.2359 | -51755.7344 | -53783.5671 | -60664.6685 | -60867.2175 | -63491.1207 | -59739.8155 | -57129.4333 | -57270.065 | -57933.595 | -54145.3061 | -56534.8967 | -56533.3817 | -51870.2774 | -52825.2716 | -54675.2805 | -53633.6121 | -54195.3374 | -54253.4547 | -54610.2385
CAT 3406 | -117335.1163 | -120317.7498 | -113966.1789 | -98643.4037 | -97812.5859 | -87097.2586 | -100767.1773 | -102136.3949 | -100100.2882 | -99230.4115 | -91340.2978 | -96550.8508 | -99944.5267 | -94114.7316 | -84997.1507 | -82306.4021 | -83468.6639 | -82057.9919 | -82285.9283 | -83831.1837
SD 60 | -5785.7305 | -5069.5822 | -6016.3309 | -4518.9098 | -3017.8017 | -3233.1852 | -2698.0917 | -4977.3957 | -4460.6899 | -4383.2377 | -5490.8503 | -5749.5182 | -7069.7792 | -6282.795 | -11668.3869 | -12019.1543 | -11708.5476 | -13205.1576 | -12229.3559 | -11423.5215
CMS | -324.5301 | -192.3154 | -7.9266 | -17.1217 | -0.16457 | -0.17142 | -164.6684 | -41.3197 | -157.9761 | -0.16457 | -0.17142 | -102.9495 | -98.4445 | -77.1058 | -662.1432 | -758.222 | -682.515 | -750.9812 | -864.1885 | -632.5625
Deasil Fuel use (Gal/year) | 110638.8 | 110638.8 | 110638.8 | 104944.8 | 104857.2 | 92593.2 | 98725.2 | 98725.2 | 93994.8 | 93907.2 | 77350.8 | 88388.4 | 88388.4 | 73233.6 | 59130 | 31360.8 | 31536 | 30222 | 30922.8 | 27944.4
Heating Fuel use (Gal/year) | 27710.8243 | 27710.9415 | 27710.8294 | 28104.771 | 28104.8137 | 29177.9152 | 28665.9737 | 28666.0113 | 29118.272 | 29118.2852 | 30627.264 | 29675.8242 | 29675.8059 | 31066.4923 | 32473.8696 | 35450.5158 | 35415.5591 | 35604.2822 | 35519.3911 | 35872.3472
Total Fuel usage (Gal/year) | 138349.6243 | 138349.7415 | 138349.6294 | 133049.571 | 132962.0137 | 121771.1152 | 127391.1737 | 127391.2113 | 123113.072 | 123025.4852 | 107978.064 | 118064.2242 | 118064.2059 | 104300.0923 | 91603.8696 | 66811.3158 | 66951.5591 | 65826.2822 | 66442.1911 | 63816.7472
New Wind Turbines (#) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 5 | 5 | 5 | 5 | 5
New 100kW Solar Fields (#) | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 2 | 2 | 3 | 3 | 5
Wind Replacement Cost (per replacement) | 0 | 0 | 0 | 0 | 0 | -560000 | 0 | 0 | 0 | 0 | -560000 | 0 | 0 | -560000 | -1092000 | -2520000 | -2520000 | -2520000 | -2520000 | -2520000
Wind Replacement NPV (Turbines are replaced every 20 years: this means that the first replacement is out of the time horizon for this analysis and so the replacement cost is not used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Replacement NPV (converter only after 10 years) | 0 | 0 | 0 | -63211.8617 | -63211.8617 | 0 | -126423.7234 | -126423.7234 | -189635.5851 | -189635.5851 | -189635.5851 | -316059.3085 | -316059.3085 | -316059.3085 | -316059.3085 | -126423.7234 | -126423.7234 | -189635.5851 | -189635.5851 | -316059.3085
Wind O&M Cost per year ($/year) | 0 | 0 | 0 | -17500 | -17500 | 0 | -34562.5 | -34562.5 | -51187.5 | -51187.5 | -51187.5 | -83125 | -83125 | -83125 | -83125 | -34562.5 | -34562.5 | -51187.5 | -51187.5 | -83125
Solar O&M Cost per year ($/year) | 0 | 0 | 0 | -4730.4 | -4730.4 | 0 | -9460.8 | -9460.8 | -14191.2 | -14191.2 | -14191.2 | -23652 | -23652 | -23652 | -23652 | -9460.8 | -9460.8 | -14191.2 | -14191.2 | -23652
Gen + Wind + Solar O&M + Genorator Replacement Cost
Year
1 | -191229.1033 | -193122.402 | -189155.7941 | -200240.5931 | -197856.241 | -166896.1899 | -221520.3797 | -222637.9479 | -241463.5828 | -240952.9209 | -229483.4974 | -279552.4256 | -284740.0071 | -272470.1167 | -270119.2103 | -206880.2107 | -206616.1583 | -228761.8913 | -228115.8403 | -270435.9733
2 | -180251.7705 | -182036.3861 | -178297.4777 | -188745.9639 | -186498.4833 | -157315.6658 | -208804.2037 | -209857.6189 | -227602.5854 | -227121.2375 | -216310.2058 | -263504.9727 | -268394.7659 | -256829.2173 | -254613.2626 | -195004.4403 | -194755.5456 | -215630.0229 | -215021.0579 | -254911.8421
3 | -175001.7189 | -176734.3554 | -173104.3473 | -183248.5087 | -181066.4887 | -152733.6562 | -202722.5278 | -203745.2611 | -220973.3839 | -220506.0558 | -210009.9086 | -255830.0706 | -260577.4426 | -249348.7547 | -247197.3424 | -189324.6993 | -189083.0539 | -209349.5368 | -208758.3086 | -247487.2253
4 | -169904.5815 | -171586.7528 | -168062.4731 | -177911.1735 | -175792.7074 | -148285.1031 | -196817.9882 | -197810.9331 | -214537.2659 | -214083.5494 | -203893.1151 | -248378.7093 | -252987.8084 | -242086.1696 | -239997.4198 | -183810.3877 | -183575.7805 | -203251.9775 | -202677.9695 | -240278.8595
5 | -164955.9043 | -166589.0804 | -163167.4496 | -172729.2946 | -170672.5315 | -143966.1195 | -191085.4254 | -192049.4496 | -208288.6077 | -207848.1062 | -197954.4807 | -241144.378 | -245619.2314 | -235035.1161 | -233007.2037 | -178456.6871 | -178228.9131 | -197332.017 | -196774.7277 | -233280.4462
6 | -160151.3634 | -161736.9713 | -158414.9996 | -167698.3443 | -165701.4869 | -139772.9315 | -185519.8305 | -186455.7763 | -202221.9492 | -201794.2778 | -192188.8162 | -234120.7553 | -238465.2732 | -228189.4331 | -226220.5861 | -173258.9195 | -173037.7797 | -191584.4825 | -191043.4249 | -226485.8701
7 | -155486.7606 | -157026.1857 | -153800.9705 | -162813.9265 | -160875.23 | -135701.8753 | -180116.3403 | -181025.0255 | -196331.9895 | -195916.7746 | -186591.0837 | -227301.7042 | -231519.6827 | -221543.139 | -219631.637 | -168212.5432 | -167997.8444 | -186004.3519 | -185479.0533 | -219889.1942
8 | -150958.02 | -152452.6075 | -149321.3306 | -158071.7733 | -156189.5437 | -131749.3935 | -174870.2333 | -175752.452 | -190613.582 | -190210.4608 | -181156.392 | -220681.2662 | -224776.391 | -215090.4262 | -213234.599 | -163313.1487 | -163104.7033 | -180586.7494 | -180076.7508 | -213484.6546
9 | -146561.1845 | -148012.2403 | -144972.1656 | -153467.7411 | -151640.3337 | -127912.0325 | -169776.9255 | -170633.4485 | -185061.7301 | -184670.3503 | -175879.9922 | -214253.6565 | -218229.5058 | -208825.6565 | -207023.8825 | -158556.4551 | -158354.0809 | -175326.9412 | -174831.7969 | -207266.6549
10 | -142292.4121 | -143701.2042 | -140749.6753 | -148997.8069 | -147223.6249 | -124186.4393 | -164831.9665 | -165663.5423 | -179671.5827 | -179291.6022 | -170757.274 | -208013.2588 | -211873.3066 | -202743.3558 | -200994.0607 | -153938.3059 | -153741.8261 | -170220.3313 | -169739.6086 | -201229.7621
11 | -138147.9729 | -139515.7322 | -136650.1702 | -144658.0649 | -142935.5582 | -120569.3586 | -160031.0355 | -160838.3905 | -174438.4298 | -174069.5167 | -165783.7611 | -201954.6202 | -205702.2394 | -196838.2095 | -195139.8648 | -149454.6659 | -149263.9088 | -165262.4575 | -164795.7365 | -195368.701
12 | -134124.2456 | -135452.1672 | -132670.0682 | -140444.7232 | -138772.3866 | -117057.6297 | -155369.9374 | -156153.7772 | -169357.6988 | -168999.5308 | -160955.1079 | -196072.4467 | -199710.9121 | -191105.0578 | -189456.1794 | -145101.6174 | -144916.4163 | -160448.9879 | -159995.8607 | -189678.3505
13 | -130217.7141 | -131506.9584 | -128805.8914 | -136354.1002 | -134730.4724 | -113648.1841 | -150844.5994 | -151605.609 | -164424.9503 | -164077.2144 | -156267.095 | -190361.5988 | -193894.0894 | -185538.8911 | -183938.0382 | -140875.3567 | -140695.5499 | -155775.7164 | -155335.7871 | -184153.7384
14 | -126424.9652 | -127676.6587 | -125054.2635 | -132382.6216 | -130806.2839 | -110338.0429 | -146451.0674 | -147189.9116 | -159635.8741 | -159298.2664 | -151715.6263 | -184817.0862 | -188246.6887 | -180134.8457 | -178580.6197 | -136772.191 | -136597.6212 | -151238.5596 | -150811.4438 | -178790.0373
15 | -122742.6846 | -123957.921 | -121411.9063 | -128526.8171 | -126996.3921 | -107124.3135 | -142185.5023 | -142902.8268 | -154986.2855 | -154658.511 | -147296.7245 | -179434.0643 | -182763.7755 | -174888.1997 | -173379.2424 | -132788.5349 | -132619.0497 | -146833.553 | -146418.8775 | -173582.5605
16 | -119167.655 | -120347.4962 | -117875.6372 | -124783.3175 | -123297.4681 | -104004.1878 | -138044.177 | -138740.6086 | -150472.1218 | -150153.8942 | -143006.5287 | -174207.8294 | -177440.5587 | -169794.3686 | -168329.3615 | -128920.9077 | -128756.359 | -142556.8476 | -142154.25 | -168526.7577
17 | -115696.7524 | -116842.2293 | -114442.3662 | -121148.852 | -119706.2797 | -100974.9396 | -134023.4728 | -134699.62 | -146089.4387 | -145780.4798 | -138841.29 | -169133.8149 | -172272.3871 | -164848.9016 | -163426.5646 | -125165.9298 | -125006.1737 | -138404.7064 | -138013.8349 | -163618.2114
18 | -112326.9441 | -113439.0575 | -111109.0934 | -117620.2446 | -116219.689 | -98033.922 | -130119.8765 | -130776.3301 | -141834.4065 | -141534.4464 | -134797.3689 | -164207.5873 | -167254.7448 | -160047.4773 | -158666.5676 | -121520.3202 | -121365.2172 | -134373.5014 | -133994.0145 | -158852.6324
19 | -109055.2855 | -110135.0073 | -107872.9062 | -114194.4123 | -112834.6495 | -95178.565 | -126329.9772 | -126967.3107 | -137703.3073 | -137412.0839 | -130871.2319 | -159424.8421 | -162383.2473 | -155385.9003 | -154045.2112 | -117980.8934 | -117830.308 | -130459.7101 | -130091.2762 | -154225.8567
20 | -105878.918 | -106927.1916 | -104730.9769 | -110868.3614 | -109548.2034 | -92406.3738 | -122650.4633 | -123269.2337 | -133692.5313 | -133409.7902 | -127059.4485 | -154781.4001 | -157653.6382 | -150860.0973 | -149558.4575 | -114544.5567 | -114398.3573 | -126659.9127 | -126302.2099 | -149733.8415
Total Gen O&M + Replacement Cost | -2850575.9565 | -2878798.6051 | -2819669.963 | -2984906.6406 | -2949364.054 | -2487854.9234 | -3302115.9297 | -3318775.0734 | -3599401.3032 | -3591789.0692 | -3420818.9486 | -4167176.4871 | -4244505.696 | -4061603.334 | -4067717.571 | -3125039.0314 | -3121102.9071 | -3451220.5144 | -3441590.0898 | -4072439.4296
Diesel Fuel Cost
Year
1 | -792542.604 | -792542.604 | -792542.604 | -751754.584 | -751127.076 | -663275.956 | -707201.516 | -707201.516 | -673316.084 | -672688.576 | -554089.564 | -633155.572 | -633155.572 | -524596.688 | -423567.9 | -224647.864 | -225902.88 | -216490.26 | -221510.324 | -200175.052
2 | -747047.4163 | -747047.4163 | -747047.4163 | -708600.7956 | -708009.3091 | -625201.2028 | -666605.2559 | -666605.2559 | -634664.9863 | -634073.4999 | -522282.5563 | -596809.852 | -596809.852 | -494482.6921 | -399253.3698 | -211752.1576 | -212935.1305 | -204062.8334 | -208794.7252 | -188684.1851
3 | -725288.7537 | -725288.7537 | -725288.7537 | -687961.9374 | -687387.6787 | -606991.459 | -647189.5688 | -647189.5688 | -616179.5984 | -615605.3397 | -507070.443 | -579427.0408 | -579427.0408 | -480080.2835 | -387624.6309 | -205584.619 | -206733.1365 | -198119.2558 | -202713.3255 | -183188.5292
4 | -704163.8386 | -704163.8386 | -704163.8386 | -667924.2111 | -667366.6784 | -589312.0961 | -628339.3872 | -628339.3872 | -598232.6198 | -597675.0871 | -492301.401 | -562550.525 | -562550.525 | -466097.3627 | -376334.5931 | -199596.7175 | -200711.783 | -192348.792 | -196809.0539 | -177852.941
5 | -683654.2122 | -683654.2122 | -683654.2122 | -648470.1079 | -647928.8139 | -572147.6661 | -610038.24 | -610038.24 | -580808.3687 | -580267.0748 | -477962.5252 | -546165.5583 | -546165.5583 | -452521.7113 | -365373.3913 | -193783.2209 | -194865.8087 | -186746.4 | -191076.7513 | -172672.7583
6 | -663741.9536 | -663741.9536 | -663741.9536 | -629582.629 | -629057.1009 | -555483.171 | -592270.136 | -592270.136 | -563891.6201 | -563366.0921 | -464041.2866 | -530257.8236 | -530257.8236 | -439341.4673 | -354731.4479 | -188139.0494 | -189190.1055 | -181307.1845 | -185511.409 | -167643.4546
7 | -644409.6637 | -644409.6637 | -644409.6637 | -611245.2709 | -610735.0494 | -539304.0495 | -575019.5495 | -575019.5495 | -547467.5924 | -546957.3709 | -450525.521 | -514813.421 | -514813.421 | -426545.1139 | -344399.464 | -182659.2713 | -183679.7141 | -176026.3927 | -180108.1641 | -162760.6356
8 | -625640.4502 | -625640.4502 | -625640.4502 | -593442.0105 | -592946.6499 | -523596.1646 | -558271.4073 | -558271.4073 | -531521.9343 | -531026.5737 | -437403.4185 | -499818.8553 | -499818.8553 | -414121.4698 | -334368.4116 | -177339.0983 | -178329.8195 | -170899.4104 | -174862.2953 | -158020.0345
9 | -607417.9128 | -607417.9128 | -607417.9128 | -576157.2918 | -575676.3592 | -508345.7908 | -542011.075 | -542011.075 | -516040.7129 | -515559.7803 | -424663.5131 | -485261.0246 | -485261.0246 | -402059.6794 | -324629.5258 | -172173.8819 | -173135.7471 | -165921.7577 | -169769.2187 | -153417.5093
10 | -589726.1289 | -589726.1289 | -589726.1289 | -559376.0115 | -558909.0866 | -493539.6028 | -526224.3447 | -526224.3447 | -501010.4009 | -500543.476 | -412294.6729 | -471127.2083 | -471127.2083 | -390349.2033 | -315174.2969 | -167159.1086 | -168092.9584 | -161089.0851 | -164824.4842 | -148949.0381
11 | -572549.6397 | -572549.6397 | -572549.6397 | -543083.5063 | -542630.1811 | -479164.6629 | -510897.422 | -510897.422 | -486417.865 | -485964.5398 | -400286.0902 | -457405.0566 | -457405.0566 | -378979.809 | -305994.463 | -162290.3967 | -163197.047 | -156397.17 | -160023.771 | -144610.7166
12 | -555873.4366 | -555873.4366 | -555873.4366 | -527265.5401 | -526825.4186 | -465208.4106 | -496016.9146 | -496016.9146 | -472250.3543 | -471810.2328 | -388627.272 | -444082.5792 | -444082.5792 | -367941.5622 | -297082.003 | -157563.4919 | -158443.7349 | -151841.9126 | -155362.8845 | -140398.754
13 | -539682.9482 | -539682.9482 | -539682.9482 | -511908.2913 | -511480.9889 | -451658.651 | -481569.82 | -481569.82 | -458495.4896 | -458068.1872 | -377308.0311 | -431148.1352 | -431148.1352 | -357224.8176 | -288429.1291 | -152974.264 | -153828.8688 | -147419.3326 | -150837.752 | -136309.4699
14 | -523964.0274 | -523964.0274 | -523964.0274 | -496998.3411 | -496583.4844 | -438503.5447 | -467543.5145 | -467543.5145 | -445141.2521 | -444726.3954 | -366318.4768 | -418590.4225 | -418590.4225 | -346820.2113 | -280028.2807 | -148518.7029 | -149348.4164 | -143125.5657 | -146444.4194 | -132339.2912
15 | -508702.9392 | -508702.9392 | -508702.9392 | -482522.6613 | -482119.8877 | -425731.5968 | -453925.7423 | -453925.7423 | -432175.9729 | -431773.1994 | -355649.0066 | -406398.4684 | -406398.4684 | -336718.6518 | -271872.1171 | -144192.9155 | -144998.4625 | -138956.8599 | -142179.0479 | -128484.7487
16 | -493886.3487 | -493886.3487 | -493886.3487 | -468468.6032 | -468077.5609 | -413331.6474 | -440704.6041 | -440704.6041 | -419588.3232 | -419197.281 | -345290.2977 | -394561.6199 | -394561.6199 | -326911.3124 | -263953.5118 | -139993.1218 | -140775.2063 | -134909.5727 | -138037.9106 | -124742.4745
17 | -479501.3095 | -479501.3095 | -479501.3095 | -454823.8866 | -454444.2339 | -401292.8615 | -427868.5477 | -427868.5477 | -407367.3041 | -406987.6514 | -335233.2987 | -383069.5338 | -383069.5338 | -317389.6237 | -256265.5454 | -135915.6522 | -136674.9576 | -130980.1677 | -134017.3889 | -121109.1985
18 | -465535.2519 | -465535.2519 | -465535.2519 | -441576.5889 | -441207.9941 | -389604.7199 | -415406.357 | -415406.357 | -395502.237 | -395133.6421 | -325469.222 | -371912.1688 | -371912.1688 | -308145.2657 | -248801.5004 | -131956.9439 | -132694.1336 | -127165.2113 | -130113.9698 | -117581.7461
19 | -451975.9727 | -451975.9727 | -451975.9727 | -428715.1348 | -428357.2758 | -378257.0096 | -403307.1427 | -403307.1427 | -383982.7543 | -383624.8953 | -315989.536 | -361079.7755 | -361079.7755 | -299170.1609 | -241554.8548 | -128113.5378 | -128829.2559 | -123461.3702 | -126324.2426 | -114157.0351
20 | -438811.624 | -438811.624 | -438811.624 | -416228.2863 | -415880.8503 | -367239.8152 | -391560.3327 | -391560.3327 | -372798.7906 | -372451.3546 | -306785.9572 | -350562.8888 | -350562.8888 | -290456.4669 | -234519.2765 | -124382.0755 | -125076.9475 | -119865.408 | -122644.8957 | -110832.0729
Total Diesel Fuel Cost | -11814116.432 | -11814116.432 | -11814116.432 | -11206105.6893 | -11196751.6778 | -9887190.0781 | -10541970.878 | -10541970.878 | -10036854.2609 | -10027500.2495 | -8259592.0898 | -9438197.5296 | -9438197.5296 | -7819953.5528 | -6313957.7131 | -3348736.0908 | -3367444.1136 | -3227133.9422 | -3301966.0337 | -2983929.6451
Heating Fuel Cost
Year
1 | -221409.4865 | -221410.4224 | -221409.5272 | -224557.1199 | -224557.4617 | -233131.5426 | -229041.1296 | -229041.4307 | -232654.9932 | -232655.0989 | -244711.8392 | -237109.8355 | -237109.689 | -248221.2732 | -259466.2184 | -283249.6209 | -282970.3174 | -284478.2146 | -283799.9351 | -286620.0543
2 | -208699.6762 | -208700.5584 | -208699.7145 | -211666.6226 | -211666.9448 | -219748.8383 | -215893.2317 | -215893.5156 | -219299.6448 | -219299.7445 | -230664.3785 | -223498.7609 | -223498.6228 | -233972.3567 | -244571.796 | -266989.9339 | -266726.6636 | -268148.0013 | -267508.6579 | -270166.8906
3 | -202621.0448 | -202621.9013 | -202621.0821 | -205501.5753 | -205501.8881 | -213348.3867 | -209605.0794 | -209605.3549 | -212912.2765 | -212912.3733 | -223945.9986 | -216989.0883 | -216988.9542 | -227157.6279 | -237448.3456 | -259213.5281 | -258957.9258 | -260337.8654 | -259717.1436 | -262297.9521
4 | -196719.461 | -196720.2925 | -196719.4972 | -199516.0926 | -199516.3963 | -207134.3561 | -203500.0771 | -203500.3446 | -206710.9481 | -206711.042 | -217423.2996 | -210669.0177 | -210668.8876 | -220541.3863 | -230532.3744 | -251663.6195 | -251415.462 | -252755.2091 | -252152.5666 | -254658.2059
5 | -190989.768 | -190990.5753 | -190989.8031 | -193704.9442 | -193705.2391 | -201101.3166 | -197572.8903 | -197573.1501 | -200690.2408 | -200690.332 | -211090.5821 | -204533.0269 | -204532.9006 | -214117.8507 | -223817.8392 | -244333.6112 | -244092.6815 | -245393.4069 | -244808.317 | -247240.9766
6 | -185426.9592 | -185427.743 | -185426.9933 | -188063.0527 | -188063.3389 | -195243.9967 | -191818.3401 | -191818.5923 | -194844.894 | -194844.9826 | -204942.3127 | -198575.7543 | -198575.6316 | -207881.4085 | -217298.873 | -237217.0982 | -236983.1859 | -238246.0261 | -237677.9777 | -240039.7831
7 | -180026.174 | -180026.9349 | -180026.2071 | -182585.488 | -182585.7659 | -189557.2783 | -186231.3982 | -186231.643 | -189169.8 | -189169.886 | -198973.1192 | -192791.9945 | -192791.8754 | -201826.6102 | -210969.7796 | -230307.8624 | -230080.763 | -231306.8215 | -230755.3182 | -233048.3331
8 | -174782.6932 | -174783.432 | -174782.7253 | -177267.4641 | -177267.7339 | -184036.1925 | -180807.1827 | -180807.4204 | -183660 | -183660.0835 | -193177.7856 | -187176.6937 | -187176.578 | -195948.1652 | -204825.0288 | -223599.8664 | -223379.3816 | -224569.7296 | -224034.2895 | -226260.5176
9 | -169691.9351 | -169692.6524 | -169691.9663 | -172104.3341 | -172104.596 | -178675.9151 | -175540.9541 | -175541.1849 | -178310.6796 | -178310.7607 | -187551.2481 | -181724.9453 | -181724.833 | -190240.9371 | -198859.2512 | -217087.2489 | -216873.186 | -218028.8637 | -217509.0189 | -219670.4054
10 | -164749.4516 | -164750.148 | -164749.4819 | -167091.5865 | -167091.8408 | -173471.7622 | -170428.1108 | -170428.3348 | -173117.1647 | -173117.2434 | -182088.5904 | -176431.9857 | -176431.8767 | -184699.9389 | -193067.2342 | -210764.3193 | -210556.4913 | -211678.5084 | -211173.8048 | -213272.2383
11 | -159950.9239 | -159951.6 | -159950.9533 | -162224.8412 | -162225.0882 | -168419.1866 | -165464.1852 | -165464.4027 | -168074.9172 | -168074.9935 | -176785.0392 | -171293.19 | -171293.0842 | -179320.3291 | -187443.9167 | -204625.5527 | -204423.7779 | -205513.115 | -205023.1114 | -207060.4255
12 | -155292.1591 | -155292.8155 | -155292.1876 | -157499.8459 | -157500.0856 | -163513.7734 | -160644.84 | -160645.0512 | -163179.5312 | -163179.6054 | -171635.9604 | -166304.068 | -166303.9652 | -174097.4069 | -181984.3852 | -198665.5852 | -198469.6873 | -199527.2961 | -199051.5645 | -201029.5393
13 | -150769.0865 | -150769.7238 | -150769.1142 | -152912.4717 | -152912.7045 | -158751.2363 | -155965.8641 | -155966.0691 | -158426.7294 | -158426.8013 | -166636.8548 | -161460.2602 | -161460.1604 | -169026.6086 | -176683.8691 | -192879.2089 | -192689.0168 | -193715.8214 | -193253.9461 | -195174.31
14 | -146377.7539 | -146378.3726 | -146377.7808 | -148458.7104 | -148458.9364 | -154127.4139 | -151423.169 | -151423.3681 | -153812.3586 | -153812.4285 | -161783.3542 | -156757.5342 | -156757.4373 | -164103.5035 | -171537.737 | -187261.3679 | -187076.7154 | -188073.613 | -187625.1904 | -189489.6214
15 | -142114.3242 | -142114.9249 | -142114.3503 | -144134.6703 | -144134.8897 | -149638.2659 | -147012.7855 | -147012.9787 | -149332.387 | -149332.4548 | -157071.2176 | -152191.7807 | -152191.6867 | -159323.7898 | -166541.4922 | -181807.1533 | -181627.879 | -182595.7408 | -182160.379 | -183970.5062
16 | -137975.072 | -137975.6552 | -137975.0974 | -139936.5731 | -139936.7861 | -145279.8698 | -142730.8597 | -142731.0473 | -144982.9 | -144982.9659 | -152496.3278 | -147759.0104 | -147758.9191 | -154683.2911 | -161690.7691 | -176511.7993 | -176337.7466 | -177277.4183 | -176854.7369 | -178612.1419
17 | -133956.3806 | -133956.9468 | -133956.4052 | -135860.7506 | -135860.9574 | -141048.4173 | -138573.6502 | -138573.8323 | -140760.0971 | -140760.161 | -148054.6872 | -143455.3499 | -143455.2613 | -150177.9525 | -156981.3293 | -171370.6789 | -171201.6957 | -172113.9983 | -171703.6281 | -173409.8465
18 | -130054.7384 | -130055.2882 | -130054.7623 | -131903.6413 | -131903.8421 | -136940.211 | -134537.5244 | -134537.7013 | -136660.2884 | -136660.3505 | -143742.4147 | -139277.0388 | -139276.9527 | -145803.8374 | -152409.0575 | -166379.2999 | -166215.2386 | -167100.9692 | -166702.5515 | -168359.0743
19 | -126266.7363 | -126267.2701 | -126266.7595 | -128061.7877 | -128061.9826 | -132951.6612 | -130618.9558 | -130619.1275 | -132679.8917 | -132679.952 | -139555.7425 | -135220.426 | -135220.3424 | -141557.1237 | -147969.9588 | -161533.3009 | -161374.018 | -162233.9507 | -161847.1374 | -163455.412
20 | -122589.0644 | -122589.5826 | -122589.0869 | -124331.8327 | -124332.022 | -129079.2827 | -126814.5201 | -126814.6869 | -128815.4288 | -128815.4873 | -135491.0121 | -131281.967 | -131281.8859 | -137434.1007 | -143660.1541 | -156828.4475 | -156673.8039 | -157508.69 | -157133.1431 | -158694.5747
Total Heating Fuel Cost | -3300462.8889 | -3300476.8399 | -3300463.4954 | -3347383.4051 | -3347388.5002 | -3475198.9033 | -3414224.7479 | -3414229.2365 | -3468095.1712 | -3468096.747 | -3647821.7645 | -3534501.7278 | -3534499.5442 | -3700135.4979 | -3867759.4096 | -4222289.1035 | -4218125.6374 | -4240603.2593 | -4230492.4177 | -4272530.8089
Total Net Present Cost | -21005872.4734 | -21119109.073 | -21094967.0864 | -21192324.7926 | -21267433.2898 | -19840961.1008 | -21475452.475 | -21612116.1073 | -21884703.5164 | -21987738.8469 | -21058585.5841 | -23046652.2491 | -23243979.2744 | -22438468.8893 | -21891211.1983 | -18663205.1451 | -18758813.5776 | -19449310.4971 | -19589401.3222 | -20985676.3882
Marginal Net Present Value (NPC-Baseline) | -21162881535.2629 | -21162994771.8625 | -21162970629.8759 | -21163067987.5821 | -21163143096.0793 | -21161716623.8903 | -21163351115.2645 | -21163487778.8968 | -21163760366.3059 | -21163863401.6364 | -21162934248.3736 | -21164922315.0386 | -21165119642.0639 | -21164314131.6787 | -21163766873.9878 | -21160538867.9346 | -21160634476.3671 | -21161324973.2866 | -21161465064.1117 | -21162861339.1777
Net Reduction in Imported Fuel | 25.65% | 25.65% | 25.65% | 28.5% | 28.54% | 34.56% | 31.54% | 31.54% | 33.84% | 33.88% | 41.97% | 36.55% | 36.55% | 43.95% | 50.77% | 64.09% | 64.02% | 64.62% | 64.29% | 65.7%
Marginal NPV = NPC - NPC(baseline) - capital investment | Highest NPV Cases
Marginal NPV (Utility Only) | 1806858.6998 | 1693636.0512 | 1717764.6934 | 1667326.8968 | 1592223.4948 | 3146506.0868 | 1451040.5573 | 1314381.4135 | 1095659.9392 | 992626.1845 | 2101504.4648 | 117.7631 | -197211.4458 | 773934.893 | 1488816.4957 | 5071352.2428 | 4971580.3442 | 4303561.0466 | 4153359.3798 | 2799122.7051
Marginal NPV (Heating Customers Only) | 511955.2688 | 511941.3178 | 511954.6622 | 465034.7526 | 465029.6574 | 337219.2544 | 398193.4097 | 398188.9211 | 344322.9864 | 344321.4106 | 164596.3931 | 277916.4298 | 277918.6134 | 112282.6597 | -55341.252 | -409870.9459 | -405707.4798 | -428185.1017 | -418074.2601 | -460112.6513
Total Marginal NPV | 2318813.9686 | 2205577.369 | 2229719.3556 | 2132361.6494 | 2057253.1522 | 3483725.3412 | 1849233.967 | 1712570.3347 | 1439982.9256 | 1336947.5951 | 2266100.8579 | 278034.1929 | 80707.1676 | 886217.5527 | 1433475.2437 | 4661481.2969 | 4565872.8644 | 3875375.9449 | 3735285.1198 | 2339010.0538
Total % ROI | 176.3% | 170.6% | 170.5% | 159.4% | 155.4% | 187.3% | 145.2% | 140.7% | 131.4% | 128.4% | 140.9% | 105% | 101.4% | 113.5% | 119.6% | 159.5% | 157.6% | 146.5% | 144.3% | 125%
Normalized to Energy Efficient System
Normalized NPV (Utility Only) |  | -113222.6486 | -89094.0064 | -139531.803 | -214635.205 | 1339647.387 | -355818.1425 | -492477.2863 | -711198.7606 | -814232.5153 | 294645.765 | -1806740.9367 | -2004070.1456 | -1032923.8068 | -318042.2041 | 3264493.543 | 3164721.6444 | 2496702.3468 | 2346500.68 | 992264.0052
Normalized NPV (Heating Customers Only) |  | -13.951 | -0.60657 | -46920.5162 | -46925.6114 | -174736.0144 | -113761.8591 | -113766.3476 | -167632.2823 | -167633.8582 | -347358.8757 | -234038.839 | -234036.6553 | -399672.609 | -567296.5208 | -921826.2147 | -917662.7486 | -940140.3704 | -930029.5288 | -972067.92
Normalized Total NPV |  | -113236.5996 | -89094.613 | -186452.3192 | -261560.8164 | 1164911.3726 | -469580.0016 | -606243.6339 | -878831.043 | -981866.3735 | -52713.1106 | -2040779.7757 | -2238106.801 | -1432596.4158 | -885338.7248 | 2342667.3283 | 2247058.8958 | 1556561.9763 | 1416471.1512 | 20196.0852
Normalized % ROI |  | -33.22% | 25.75% | 66.1% | 60.96% | 222.6% | 55.28% | 48.18% | 43.3% | 41.21% | 97.89% | 19.97% | 16.18% | 59.07% | 79.34% | 148.8% | 146% | 129.4% | 126.3% | 100.3%
No Generator
100kW Diesel
Note on A225: Author: Already Included in Purchase Cost
Note on A234: Author: If the generator utilization is less than 30% then a new small generator is purchased (This assumes that the O&M costs for the generator set would not change as the O&M cost for the new generator would offset some of the O&M cost for the existing generator)
Note on B334: Author: NPV Values are normalized to the Baseline
Note on C334: Author: NPV Values are normalized to the Baseline
Note on D334: Author: NPV Values are normalized to the Baseline
Note on E334: Author: NPV Values are normalized to the Baseline
Note on F334: Author: NPV Values are normalized to the Baseline
Note on G334: Author: NPV Values are normalized to the Baseline
Note on H334: Author: NPV Values are normalized to the Baseline
Note on I334: Author: NPV Values are normalized to the Baseline
Note on J334: Author: NPV Values are normalized to the Baseline
Note on K334: Author: NPV Values are normalized to the Baseline
Note on L334: Author: NPV Values are normalized to the Baseline
Note on M334: Author: NPV Values are normalized to the Baseline
Note on N334: Author: NPV Values are normalized to the Baseline
Note on O334: Author: NPV Values are normalized to the Baseline
Note on P334: Author: NPV Values are normalized to the Baseline
Note on Q334: Author: NPV Values are normalized to the Baseline
Note on R334: Author: NPV Values are normalized to the Baseline
Note on S334: Author: NPV Values are normalized to the Baseline
Note on T334: Author: NPV Values are normalized to the Baseline
Note on U334: Author: NPV Values are normalized to the Baseline
Note on A335: Author: Value of Heating Fuel Deferred - Cost of Stove System
Note on B335: Author: NPV Values are normalized to the Baseline
Note on A341: Author: Value of Heating Fuel Deferred - Cost of Stove System

## Highlights
Highlights
Analysis using 3% discount rate
With Heating Stoves |  |  |  |  | Without Heating stoves
Low EE | Electrical Load -5% | Thermal Load -25% |  |  | Low EE | Electrical Load -5% | Thermal Load -25%
Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case | Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case
New Solar | No Generator | SG 200 | SG 500 | SG 200 | New Solar | No Generator | SG 300 | No Generator | SG 300
Hydro | No Generator | No Generator | No Generator | No Generator | Hydro | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | WG 500 | WG 500 | WG 500 | New Wind | No Generator | WG 500 | No Generator | WG 500
New Storage | No Battery | No Battery | No Battery | No Battery | New Storage | No Battery | No Battery | No Battery | No Battery
New Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | New Generator | No Generator | 100kW Diesel | No Generator | 100kW Diesel
Energy Efficiency Cost (Customers) | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | Energy Efficiency Cost (Customers) | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169
Renewable Energy Purchase Cost (Utility) | 0 | -4800000 | -6300000 | -4800000 | Renewable Energy Purchase Cost (Utility) | 0 | -5300000 | 0 | -5300000
Stove Purchase Cost (Customers) | 0 | -31875.59 | -44837.12 | -31875.59 | Stove Purchase Cost (Customers) | 0 | 0 | 0 | 0
New Generator Purchase Cost (Utility) | 0 | -41158.26 | -41158.26 | -41158.26 | New Generator Purchase Cost (Utility) | 0 | -41158.26 | 0 | -41158.26
Net Reduction in Imported Fuel | 12.1% | 58.24% | 62.98% | 58.24% | Net Reduction in Imported Fuel | 11.95% | 53.35% | 11.95% | 53.35%
Marginal NPV (Utility Only) | 322318.1437 | 4091239.8088 | 1841574.3456 | 4091239.8088 | Marginal NPV (Utility Only) | 191270.0033 | 3350161.1791 | 191270.0033 | 3350161.1791
Marginal NPV (Heating Customers Only) | 1477344.0172 | 1581892.2361 | 2222556.5619 | 1581892.2361 | Marginal NPV (Heating Customers Only) | 1453567.3184 | 414316.5591 | 1453567.3184 | 414316.5591
Total Marginal NPV | 1799662.1609 | 5673132.0448 | 4064130.9075 | 5673132.0448 | Total Marginal NPV | 1644837.3217 | 3764477.7382 | 1644837.3217 | 3764477.7382
Total % ROI | 447.1% | 206% | 159.2% | 206% | Total % ROI | 417.3% | 164.7% | 417.3% | 164.7%
Medium EE | Electrical Load -10% | Thermal Load -35% |  |  | Medium EE | Electrical Load -10% | Thermal Load -35%
Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case | Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case
New Solar | No Generator | SG 200 | SG 500 | SG 200 | New Solar | No Generator | SG 200 | No Generator | SG 200
Hydro | No Generator | No Generator | No Generator | No Generator | Hydro | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | WG 500 | WG 500 | WG 500 | New Wind | No Generator | WG 500 | No Generator | WG 500
New Storage | No Battery | No Battery | No Battery | No Battery | New Storage | No Battery | No Battery | No Battery | No Battery
New Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | New Generator | No Generator | 100kW Diesel | No Generator | 100kW Diesel
Energy Efficiency Cost (Customers) | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | Energy Efficiency Cost (Customers) | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899
Renewable Energy Purchase Cost (Utility) | 0 | -4800000 | -6300000 | -4800000 | Renewable Energy Purchase Cost (Utility) | 0 | -4800000 | 0 | -4800000
Stove Purchase Cost (Customers) | 0 | -34482.88 | -47876.44 | -34482.88 | Stove Purchase Cost (Customers) | 0 | 0 | 0 | 0
New Generator Purchase Cost (Utility) | 0 | -41158.26 | -41158.26 | -41158.26 | New Generator Purchase Cost (Utility) | 0 | -41158.26 | 0 | -41158.26
Net Reduction in Imported Fuel | 18.95% | 64.71% | 69.5% | 64.71% | Net Reduction in Imported Fuel | 18.9% | 57.83% | 18.9% | 57.83%
Marginal NPV (Utility Only) | 1176325.8184 | 4636685.8586 | 2355182.0562 | 4636685.8586 | Marginal NPV (Utility Only) | 1077750.0826 | 4429355.0642 | 819389.5883 | 4429355.0642
Marginal NPV (Heating Customers Only) | 1353967.5006 | 1642135.4682 | 2304703.2888 | 1642135.4682 | Marginal NPV (Heating Customers Only) | 1331860.0482 | 370585.1304 | 166487.9604 | 370585.1304
Total Marginal NPV | 2530293.3189 | 6278821.3268 | 4659885.345 | 6278821.3268 | Total Marginal NPV | 2409610.1308 | 4799940.1946 | 985877.5487 | 4799940.1946
Total % ROI | 278.9% | 200.5% | 160% | 200.5% | Total % ROI | 270.4% | 177.2% | 169.7% | 177.2%
High EE | Electrical Load -15% | Thermal Load -45% |  |  | High EE | Electrical Load -15% | Thermal Load -45%
Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case | Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case
New Solar | No Generator | SG 100 | SG 500 | SG 100 | New Solar | No Generator | SG 200 | No Generator | SG 200
Hydro | No Generator | No Generator | No Generator | No Generator | Hydro | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | WG 500 | WG 500 | WG 500 | New Wind | No Generator | WG 500 | No Generator | WG 500
New Storage | No Battery | No Battery | Bat 100/100 | No Battery | New Storage | No Battery | No Battery | No Battery | No Battery
New Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | New Generator | No Generator | 100kW Diesel | No Generator | 100kW Diesel
Energy Efficiency Cost (Customers) | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | Energy Efficiency Cost (Customers) | -3040717.196 | -3040717.196 | -3040717.2839 | -3040717.196
Renewable Energy Purchase Cost (Utility) | 0 | -4300000 | -6420000 | -4300000 | Renewable Energy Purchase Cost (Utility) | 0 | -4800000 | 0 | -4800000
Stove Purchase Cost (Customers) | 0 | -33002.13 | -50234.31 | -33002.13 | Stove Purchase Cost (Customers) | 0 | 0 | 0 | 0
New Generator Purchase Cost (Utility) | 0 | -41158.26 | -41158.26 | -41158.26 | New Generator Purchase Cost (Utility) | 0 | -41158.26 | 0 | -41158.26
Net Reduction in Imported Fuel | 25.74% | 68.68% | 75.03% | 68.68% | Net Reduction in Imported Fuel | 25.65% | 64.09% | 25.74% | 64.09%
Marginal NPV (Utility Only) | 1854284.5272 | 5718748.8035 | 2581060.944 | 5718748.8035 | Marginal NPV (Utility Only) | 1806858.6998 | 5071352.2428 | 1464924.3456 | 5071352.2428
Marginal NPV (Heating Customers Only) | 532501.4534 | 835282.5497 | 1681551.4337 | 835282.5497 | Marginal NPV (Heating Customers Only) | 511955.2688 | -409870.9459 | -962379.1281 | -409870.9459
Total Marginal NPV | 2386785.9806 | 6554031.3532 | 4262612.3777 | 6554031.3532 | Total Marginal NPV | 2318813.9686 | 4661481.2969 | 502545.2175 | 4661481.2969
Total % ROI | 178.5% | 188.9% | 144.8% | 188.9% | Total % ROI | 176.3% | 159.5% | 116.5% | 159.5%
Analysis using 7% discount rate
With Heating Stoves |  |  |  |  | Without Heating stoves
Low EE | Electrical Load -5% | Thermal Load -25% |  |  | Low EE | Electrical Load -5% | Thermal Load -25%
Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case | Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case
New Solar | No Generator | SG 200 | SG 500 | SG 200 | New Solar | No Generator | No Generator | No Generator | No Generator
Hydro | No Generator | No Generator | No Generator | No Generator | Hydro | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | WG 500 | WG 500 | WG 500 | New Wind | No Generator | WG 100 | No Generator | WG 100
New Storage | No Battery | No Battery | No Battery | No Battery | New Storage | No Battery | No Battery | Bat 10/10 | No Battery
New Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | New Generator | No Generator | No Generator | No Generator | No Generator
Energy Efficiency Cost (Customers) | -518433.4013 | -518433.4013 | -518433.4013 | -518433.4013 | Energy Efficiency Cost (Customers) | -518433.4169 | -518433.4169 | -518433.4169 | -518433.4169
Renewable Energy Purchase Cost (Utility) | 0 | -4800000 | -6300000 | -4800000 | Renewable Energy Purchase Cost (Utility) | 0 | -950000 | -57000 | -950000
Stove Purchase Cost (Customers) | 0 | -31875.59 | -44837.12 | -31875.59 | Stove Purchase Cost (Customers) | 0 | 0 | 0 | 0
New Generator Purchase Cost (Utility) | 0 | -41158.26 | -41158.26 | -41158.26 | New Generator Purchase Cost (Utility) | 0 | 0 | 0 | 0
Net Reduction in Imported Fuel | 12.1% | 58.24% | 62.98% | 58.24% | Net Reduction in Imported Fuel | 11.95% | 21.12% | 12% | 21.12%
Marginal NPV (Utility Only) | 230483.7449 | 1553496.4674 | -471682.4026 | 1553496.4674 | Marginal NPV (Utility Only) | 136773.6428 | 962700.0489 | 164189.4105 | 962700.0489
Marginal NPV (Heating Customers Only) | 912332.7489 | 978011.3021 | 1432445.5361 | 978011.3021 | Marginal NPV (Heating Customers Only) | 895330.4712 | 766473.421 | 895376.3613 | 766473.421
Total Marginal NPV | 1142816.4939 | 2531507.7695 | 960763.1336 | 2531507.7695 | Total Marginal NPV | 1032104.114 | 1729173.4699 | 1059565.7718 | 1729173.4699
Total % ROI | 320.4% | 147.3% | 114% | 147.3% | Total % ROI | 299.1% | 217.8% | 284.1% | 217.8%
Medium EE | Electrical Load -10% | Thermal Load -35% |  |  | Medium EE | Electrical Load -10% | Thermal Load -35%
Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case | Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case
New Solar | No Generator | SG 200 | SG 500 | SG 200 | New Solar | No Generator | SG 200 | No Generator | No Generator
Hydro | No Generator | No Generator | No Generator | No Generator | Hydro | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | WG 500 | WG 500 | WG 500 | New Wind | No Generator | WG 500 | No Generator | WG 100
New Storage | No Battery | No Battery | No Battery | No Battery | New Storage | No Battery | No Battery | No Battery | No Battery
New Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | New Generator | No Generator | 100kW Diesel | No Generator | No Generator
Energy Efficiency Cost (Customers) | -1414120.243 | -1414120.243 | -1414120.243 | -1414120.243 | Energy Efficiency Cost (Customers) | -1414119.9899 | -1414119.9899 | -1414119.9899 | -1414119.9899
Renewable Energy Purchase Cost (Utility) | 0 | -4800000 | -6300000 | -4800000 | Renewable Energy Purchase Cost (Utility) | 0 | -4800000 | 0 | -950000
Stove Purchase Cost (Customers) | 0 | -34482.88 | -47876.44 | -34482.88 | Stove Purchase Cost (Customers) | 0 | 0 | 0 | 0
New Generator Purchase Cost (Utility) | 0 | -41158.26 | -41158.26 | -41158.26 | New Generator Purchase Cost (Utility) | 0 | -41158.26 | 0 | 0
Net Reduction in Imported Fuel | 18.95% | 64.71% | 69.5% | 64.71% | Net Reduction in Imported Fuel | 18.9% | 57.83% | 18.9% | 27.89%
Marginal NPV (Utility Only) | 841168.8425 | 1943534.8524 | -104411.0253 | 1943534.8524 | Marginal NPV (Utility Only) | 770679.1566 | 1795276.4348 | 770679.1566 | 1354246.498
Marginal NPV (Heating Customers Only) | 576456.9634 | 772695.7387 | 1242669.6635 | 772695.7387 | Marginal NPV (Heating Customers Only) | 560648.3962 | -126741.5237 | 560648.3962 | 433507.4959
Total Marginal NPV | 1417625.8059 | 2716230.5911 | 1138258.6383 | 2716230.5911 | Total Marginal NPV | 1331327.5527 | 1668534.9111 | 1331327.5527 | 1787753.9939
Total % ROI | 200.2% | 143.5% | 114.7% | 143.5% | Total % ROI | 194.1% | 126.9% | 194.1% | 175.6%
High EE | Electrical Load -15% | Thermal Load -45% |  |  | High EE | Electrical Load -15% | Thermal Load -45%
Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case | Case Metrics | Base EE Case | Highest NPV Case for Utility | Highest NPV Case for Heat Customer | Highest Total NPV Case
New Solar | No Generator | SG 100 | SG 500 | SG 100 | New Solar | No Generator | SG 200 | No Generator | No Generator
Hydro | No Generator | No Generator | No Generator | No Generator | Hydro | No Generator | No Generator | No Generator | No Generator
New Wind | No Generator | WG 500 | WG 500 | WG 500 | New Wind | No Generator | WG 500 | No Generator | WG 100
New Storage | No Battery | No Battery | Bat 100/100 | No Battery | New Storage | No Battery | No Battery | No Battery | No Battery
New Generator | No Generator | 100kW Diesel | 100kW Diesel | 100kW Diesel | New Generator | No Generator | 100kW Diesel | No Generator | No Generator
Energy Efficiency Cost (Customers) | -3040717.2839 | -3040717.2839 | -3040717.2839 | -3040717.2839 | Energy Efficiency Cost (Customers) | -3040717.196 | -3040717.196 | -3040717.196 | -3040717.196
Renewable Energy Purchase Cost (Utility) | 0 | -4300000 | -6420000 | -4300000 | Renewable Energy Purchase Cost (Utility) | 0 | -4800000 | 0 | -950000
Stove Purchase Cost (Customers) | 0 | -33002.13 | -50234.31 | -33002.13 | Stove Purchase Cost (Customers) | 0 | 0 | 0 | 0
New Generator Purchase Cost (Utility) | 0 | -41158.26 | -41158.26 | -41158.26 | New Generator Purchase Cost (Utility) | 0 | -41158.26 | 0 | 0
Net Reduction in Imported Fuel | 25.74% | 68.68% | 75.03% | 68.68% | Net Reduction in Imported Fuel | 25.65% | 64.09% | 25.65% | 34.56%
Marginal NPV (Utility Only) | 1325964.5798 | 2856126.2881 | 22920.5721 | 2856126.2881 | Marginal NPV (Utility Only) | 1292051.2476 | 2254356.7468 | 1292051.2476 | 1979335.7587
Marginal NPV (Heating Customers Only) | -456769.9861 | -249659.7396 | 350581.7252 | -249659.7396 | Marginal NPV (Heating Customers Only) | -471462.1829 | -1130643.0645 | -471462.1829 | -596412.6759
Total Marginal NPV | 869194.5937 | 2606466.5485 | 373502.2973 | 2606466.5485 | Total Marginal NPV | 820589.0647 | 1123713.6822 | 820589.0647 | 1382923.0827
Total % ROI | 128.6% | 135.3% | 103.9% | 135.3% | Total % ROI | 127% | 114.3% | 127% | 134.7%

## NPV Plotting
Low EE
Midium EE
High EE
Low EE no Stoves
Midium EE no Stoves
High EE no Stoves

## Fuel Cost Sensitivity
| Maximum NPV | Capital Cost
low | 5673132.0448 | 5391467.2513
med | 6278821.3268 | 6289761.383
high | 6554031.3532 | 7414877.6739
low, no stove | 3764477.7382 | 5859591.6769
med, no stove | 4799940.1946 | 6255278.2499
high, no stove | 4661481.2969 | 7881875.456
Total NPV | 3%, -30% | 3%, -15% | 3%, +0% | 3%, +50% | 3%, +100% | 7%, -30% | 7%, -15% | 7%, +0% | 7%, +50% | 7%, +100%
low | 2135671.7071 | 3904401.876 | 5673132.0448 | 11568899.2743 | 17464666.5038 | 582954.5235 | 1266721.5294 | 2531507.7695 | 6747461.9031 | 10963416.0367
med | 2327047.6801 | 4302934.5035 | 6278821.3268 | 12865110.7378 | 19451400.1489 | 549273.0338 | 1303310.4577 | 2716230.5911 | 7425964.369 | 12135698.1469
high | 2341673.5693 | 4447852.4612 | 6554031.3532 | 13574627.6596 | 20595223.966 | -305086.3757 | 1100376.9659 | 2606466.5485 | 7626765.157 | 12647063.7655
low, no stove | 1684317.585 | 2341242.9157 | 3764477.7382 | 9111966.3971 | 14459455.056 | 789663.1549 | 1259418.3124 | 1729173.4699 | 4860808.3449 | 8684698.6103
med, no stove | 1725796.632 | 3049423.5232 | 4799940.1946 | 10634995.7659 | 16470051.3372 | 555432.244 | 1178026.4616 | 1800620.6792 | 5841075.2605 | 10013615.6098
high, no stove | 1322068.2954 | 2711948.206 | 4661481.2969 | 11159924.9333 | 17658368.5698 | -162837.9018 | 610042.5904 | 1382923.0827 | 5770630.571 | 10417547.4598
Capital Cost | 3%, -30% | 3%, -15% | 3%, +0% | 3%, +50% | 3%, +100% | 7%, -30% | 7%, -15% | 7%, +0% | 7%, +50% | 7%, +100%
low | 5391467.2513 | 5391467.2513 | 5391467.2513 | 5391467.2513 | 5391467.2513 | 518433.4013 | 5391467.2513 | 5391467.2513 | 5391467.2513 | 5391467.2513
med | 6289761.383 | 6289761.383 | 6289761.383 | 6289761.383 | 6289761.383 | 1414120.243 | 6289761.383 | 6289761.383 | 6289761.383 | 6289761.383
high | 7414877.6739 | 7414877.6739 | 7414877.6739 | 7414877.6739 | 7414877.6739 | 3040717.2839 | 7414877.6739 | 7414877.6739 | 7414877.6739 | 7414877.6739
low, no stove | 1468433.4169 | 1468433.4169 | 5859591.6769 | 5859591.6769 | 5859591.6769 | 1468433.4169 | 1468433.4169 | 1468433.4169 | 5859591.6769 | 5859591.6769
med, no stove | 2421119.9899 | 6255278.2499 | 6255278.2499 | 6255278.2499 | 6255278.2499 | 2421119.9899 | 2421119.9899 | 2421119.9899 | 6255278.2499 | 6255278.2499
high, no stove | 3990717.196 | 7881875.456 | 7881875.456 | 7881875.456 | 7881875.456 | 3990717.196 | 3990717.196 | 3990717.196 | 7881875.456 | 7881875.456
X-axis for plot | -30% | -15% | 0% | 50% | 100%